## Introduction
REFINERY WASTEWATER EMISSION TOOL: ICR VERSION 2.1 (RWETv2.1)
Collection System
minWindSpd
|  |  | 0.1 | m/s
The Refinery Wastewater Emissions Tool Version 1.0 (RWET) is an Excel-based model designed to help regulated facilities estimate air emissions from wastewater collection and treatment systems. Separate sheets in RWET represent individual components in a typical wastewater treatment system and can estimate emissions for that particular unit. Effluent concentrations from a particular component can then be used as inputs for the next downstream collection or treatment unit. The calculations are primarily based on those presented in EPA AP-42 but also include updates deemed more accurate in the literature. The equations are presented in Appendix B of the emission protocol document.
Air Emissions
Each sheet is set-up with a series of critical inputs, constants/variables with default values, and outputs. The following procedure should be used to reliably use RWET:
1. Determine the critical inputs of the unit listed on the corresponding sheet of RWET and record them on appropriate sheet.
2. Determine the influent concentrations of the pollutants of interest and input them into the model.
3. Review the default values of the variables and constants and make site-specific adjustments if necessary.
4. Review the chemical properties sheet and make any site-specific adjustments if necessary.
5. Record the air emissions for reporting and copy the pollutant effluent concentrations as inputs to the next downstream unit.
6. Repeat this process for the next downstream unit.
Process Wastewater
Collection System
(weirs, junction boxes, lift stations & sumps)
Oil-water Separators
Dissolved Air Floatation Units
Equalization Tanks
Biological Treatment Units
Air Emissions
Air Emissions
Air Emissions
Air Emissions
Air Emissions
Slop Oil
Biosolids
Float
Treated effluent

## POTW Discharge
This sheet is used for facilities that discharge wastewater to a POTW only. Directions: 1) Input (yellow boxes) facility wastewater flow rate and flow rate at the POTW; 2) Input (yellow boxes) constituent concentrations in the facility wastewater. The outputs (green boxes) are the pollutant concentration after dilution in the POTW wastewater. The treatment units of the POTW are then used to estimate air emissions using RWET.
INPUTS | VALUE | UNITS
Wastewater discharge flow rate (Q) | 1 | m3/s
POTW Wastewater flow rate (QPOTW) | 10 | m3/s
CONSTITUENT DISCHARGE CONCENTRATIONS TO POTW (C0) |  |  | CONSTITUENT CONCENTRATIONS AT POTW (C)
Methanol | 1 | g/m3 | Methanol | 0.090909 | g/m3
Benzene | 1 | g/m3 | Benzene | 0.090909 | g/m3
Carbon disulfide | 1 | g/m3 | Carbon disulfide | 0.090909 | g/m3
Methyl ethyl ketone | 1 | g/m3 | Methyl ethyl ketone | 0.090909 | g/m3
Naphthalene | 1 | g/m3 | Naphthalene | 0.090909 | g/m3
Cumene | 0 | g/m3 | Cumene | 0 | g/m3
Ethylbenzene | 0 | g/m3 | Ethylbenzene | 0 | g/m3
Styrene | 0 | g/m3 | Styrene | 0 | g/m3
1,3-Butadiene | 0 | g/m3 | 1,3-Butadiene | 0 | g/m3
Ethylene glycol | 0 | g/m3 | Ethylene glycol | 0 | g/m3
Methyl isobutyl ketone | 0 | g/m3 | Methyl isobutyl ketone | 0 | g/m3
Toluene | 0 | g/m3 | Toluene | 0 | g/m3
Phenol | 0 | g/m3 | Phenol | 0 | g/m3
n-Hexane | 0 | g/m3 | n-Hexane | 0 | g/m3
Cresols (total) | 0 | g/m3 | Cresols (total) | 0 | g/m3
Xylenes | 0 | g/m3 | Xylenes | 0 | g/m3
Methyl tert-butyl ether | 0 | g/m3 | Methyl tert-butyl ether | 0 | g/m3
Biphenyl, 1,1- | 0 | g/m3 | Biphenyl, 1,1- | 0 | g/m3
Carbonyl sulfide | 0 | g/m3 | Carbonyl sulfide | 0 | g/m3
Dichloroethane, 1,2- | 0 | g/m3 | Dichloroethane, 1,2- | 0 | g/m3
Diethanolamine | 0 | g/m3 | Diethanolamine | 0 | g/m3
Trimethylpentane, 2,2,4- | 0 | g/m3 | Trimethylpentane, 2,2,4- | 0 | g/m3
Compound A | 0 | g/m3 | Compound A | 0 | g/m3
Compound B | 0 | g/m3 | Compound B | 0 | g/m3
Compound C | 0 | g/m3 | Compound C | 0 | g/m3
Butane (VOC Surrogate) | 0 | g/m3 | Butane (VOC Surrogate) | 0 | g/m3

## Wastewater Collection System
This sheet is used for wastewater collection systems. Directions: 1) input the number of collection system components for each process drainage area; 2) input the process drainage area point-of-generation concentrations and flow rate (yellow boxes); 3) review the default air emissions control efficiencies and change if necessary; and 4) record the collection system air emissions and wastewater concentrations for downstream process units air emissions calculations (green boxes).
Collection System Component | Process Drainage Area #1 | Process Drainage Area #2 | Process Drainage Area #3 | Process Drainage Area #4 | Process Drainage Area #5 | Process Drainage Area #6 | Process Drainage Area #7 | Process Drainage Area #8 | Process Drainage Area #9 | Process Drainage Area #10 | Process Drainage Area #11 | Process Drainage Area #12 | Process Drainage Area #13 | Process Drainage Area #14 | Process Drainage Area #15 | Process Drainage Area #16 | Process Drainage Area #17 | Process Drainage Area #18 | Process Drainage Area #19 | Process Drainage Area #20
Number of uncontrolled drains | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Number of sealed drains | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Linear meters of open trench | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Number of uncontrolled manholes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Number of sealed manholes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Number of uncontrolled junction boxes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Number of controlled junction boxes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Number of uncontrolled lift stations | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Number of controlled lift stations | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Number of uncontrolled sumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Number of controlled sumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Collection System Component Air Emissions Control | Control Efficiency, % | Default Control Efficiency, %
Drain water seal | 95 | 95
Manhole seal | 95 | 95
Junction box water seal | 95 | 95
Lift station control (e.g., carbon adsportion) | 95 | 95
Sump control (e.g., carbon adsorption) | 95 | 95
| Process Drainage Area #1 |  |  |  | Process Drainage Area #2 |  |  |  | Process Drainage Area #3 |  |  |  | Process Drainage Area #4 |  |  |  | Process Drainage Area #5 |  |  |  | Process Drainage Area #6 |  |  |  | Process Drainage Area #7 |  |  |  | Process Drainage Area #8 |  |  |  | Process Drainage Area #9 |  |  |  | Process Drainage Area #10 |  |  |  | Process Drainage Area #11 |  |  |  | Process Drainage Area #12 |  |  |  | Process Drainage Area #13 |  |  |  | Process Drainage Area #14 |  |  |  | Process Drainage Area #15 |  |  |  | Process Drainage Area #16 |  |  |  | Process Drainage Area #17 |  |  |  | Process Drainage Area #18 |  |  |  | Process Drainage Area #19 |  |  |  | Process Drainage Area #20
Wastewater flow rate (Q) | 1 | m3/s |  |  | 0 | m3/s |  |  | 0 | m3/s |  |  | 0 | m3/s |  |  | 0 | m3/s |  |  | 0 | m3/s |  |  | 0 | m3/s |  |  | 0 | m3/s |  |  | 0 | m3/s |  |  | 0 | m3/s |  |  | 0 | m3/s |  |  | 0 | m3/s |  |  | 0 | m3/s |  |  | 0 | m3/s |  |  | 0 | m3/s |  |  | 0 | m3/s |  |  | 0 | m3/s |  |  | 0 | m3/s |  |  | 0 | m3/s |  |  | 0 | m3/s
Compound Name | POG Concentration | Units | Air Emissions | Units | POG Concentration | Units | Air Emissions | Units | POG Concentration | Units | Air Emissions | Units | POG Concentration | Units | Air Emissions | Units | POG Concentration | Units | Air Emissions | Units | POG Concentration | Units | Air Emissions | Units | POG Concentration | Units | Air Emissions | Units | POG Concentration | Units | Air Emissions | Units | POG Concentration | Units | Air Emissions | Units | POG Concentration | Units | Air Emissions | Units | POG Concentration | Units | Air Emissions | Units | POG Concentration | Units | Air Emissions | Units | POG Concentration | Units | Air Emissions | Units | POG Concentration | Units | Air Emissions | Units | POG Concentration | Units | Air Emissions | Units | POG Concentration | Units | Air Emissions | Units | POG Concentration | Units | Air Emissions | Units | POG Concentration | Units | Air Emissions | Units | POG Concentration | Units | Air Emissions | Units | POG Concentration | Units | Air Emissions | Units
Methanol | 1 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s
Benzene | 1 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s
Carbon disulfide | 1 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s
Methyl ethyl ketone | 1 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s
Naphthalene | 1 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s
Cumene | 1 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s
Ethylbenzene | 1 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s
Styrene | 1 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s
1,3-Butadiene | 1 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s
Ethylene glycol | 1 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s
Methyl isobutyl ketone | 1 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s
Toluene | 1 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s
Phenol | 1 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s
n-Hexane | 1 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s
Cresols (total) | 1 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s
Xylenes | 1 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s
Methyl tert-butyl ether | 1 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s
Biphenyl, 1,1- | 1 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s
Carbonyl sulfide | 1 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s
Dichloroethane, 1,2- | 1 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s
Diethanolamine | 1 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s
Trimethylpentane, 2,2,4- | 1 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s
Compound A | 1 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s
Compound B | 1 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s
Compound C | 1 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s | 0 | g/m3 | #NUM! | g/s
n-Butane (VOC Surrogate) | 1 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s | 0 | g/m3 | 0 | g/s
OUTPUTS
Compound Name | Total Emissions | Units | Collection System Effluent Concentration | Units | POG Total Load | Units
Methanol | 0 | g/s | 1 | g/m3 | 1 | g/s
Benzene | 0 | g/s | 1 | g/m3 | 1 | g/s
Carbon disulfide | 0 | g/s | 1 | g/m3 | 1 | g/s
Methyl ethyl ketone | 0 | g/s | 1 | g/m3 | 1 | g/s
Naphthalene | 0 | g/s | 1 | g/m3 | 1 | g/s
Cumene | 0 | g/s | 1 | g/m3 | 1 | g/s
Ethylbenzene | 0 | g/s | 1 | g/m3 | 1 | g/s
Styrene | 0 | g/s | 1 | g/m3 | 1 | g/s
1,3-Butadiene | 0 | g/s | 1 | g/m3 | 1 | g/s
Ethylene glycol | 0 | g/s | 1 | g/m3 | 1 | g/s
Methyl isobutyl ketone | 0 | g/s | 1 | g/m3 | 1 | g/s
Toluene | 0 | g/s | 1 | g/m3 | 1 | g/s
Phenol | 0 | g/s | 1 | g/m3 | 1 | g/s
n-Hexane | 0 | g/s | 1 | g/m3 | 1 | g/s
Cresols (total) | 0 | g/s | 1 | g/m3 | 1 | g/s
Xylenes | 0 | g/s | 1 | g/m3 | 1 | g/s
Methyl tert-butyl ether | 0 | g/s | 1 | g/m3 | 1 | g/s
Biphenyl, 1,1- | 0 | g/s | 1 | g/m3 | 1 | g/s
Carbonyl sulfide | 0 | g/s | 1 | g/m3 | 1 | g/s
Dichloroethane, 1,2- | 0 | g/s | 1 | g/m3 | 1 | g/s
Diethanolamine | 0 | g/s | 1 | g/m3 | 1 | g/s
Trimethylpentane, 2,2,4- | 0 | g/s | 1 | g/m3 | 1 | g/s
Compound A | #NUM! | g/s | #NUM! | g/m3 | 1 | g/s
Compound B | #NUM! | g/s | #NUM! | g/m3 | 1 | g/s
Compound C | #NUM! | g/s | #NUM! | g/m3 | 1 | g/s
n-Butane (VOC Surrogate) | 0 | g/s | 1 | g/m3 | 1 | g/s
Compound Name | fe, Drains | fe, Sealed Drains | fe, Trenches | fe, Manholes | fe, Sealed Manholes | fe, Junction Boxes | fe, Controlled Junction Boxes | fe, Lift Stations | fe, Controlled Lift Stations | fe, Sumps | fe, Controlled Sumps
Methanol | 0 | 0 | 0.0042981 | 0 | 0 | 0.012446 | 0.0006223 | 0.032528 | 0.0016264 | 0.0020798 | 0.00010399
Benzene | 0.2263 | 0.011315 | 0.039857 | 0.056902 | 0.0028451 | 0.087119 | 0.0043559 | 0.25441 | 0.012721 | 0.0049245 | 0.00024623
Carbon disulfide | 0.28543 | 0.014272 | 0.048304 | 0.072108 | 0.0036054 | 0.10486 | 0.005243 | 0.30713 | 0.015356 | 0.0056003 | 0.00028002
Methyl ethyl ketone | 0.065182 | 0.0032591 | 0.01684 | 0.015472 | 0.00077362 | 0.038785 | 0.0019392 | 0.11079 | 0.0055396 | 0.0030832 | 0.00015416
Naphthalene | 0.14066 | 0.0070329 | 0.027623 | 0.034881 | 0.001744 | 0.061427 | 0.0030714 | 0.17807 | 0.0089036 | 0.0039458 | 0.00019729
Cumene | 0.25996 | 0.012998 | 0.044666 | 0.065559 | 0.003278 | 0.097219 | 0.004861 | 0.28443 | 0.014221 | 0.0053093 | 0.00026547
Ethylbenzene | 0.23838 | 0.011919 | 0.041583 | 0.060009 | 0.0030005 | 0.090744 | 0.0045372 | 0.26519 | 0.013259 | 0.0050626 | 0.00025313
Styrene | 0.20153 | 0.010077 | 0.036319 | 0.050535 | 0.0025267 | 0.07969 | 0.0039845 | 0.23234 | 0.011617 | 0.0046415 | 0.00023208
1,3-Butadiene | 0.31658 | 0.015829 | 0.052754 | 0.080118 | 0.0040059 | 0.1142 | 0.0057102 | 0.3349 | 0.016745 | 0.0059564 | 0.00029782
Ethylene glycol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Methyl isobutyl ketone | 0.096819 | 0.004841 | 0.02136 | 0.023608 | 0.0011804 | 0.048276 | 0.0024138 | 0.13899 | 0.0069497 | 0.0034448 | 0.00017224
Toluene | 0.23239 | 0.011619 | 0.040727 | 0.058468 | 0.0029234 | 0.088946 | 0.0044473 | 0.25984 | 0.012992 | 0.0049941 | 0.00024971
Phenol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011043 | 5.5213e-05
n-Hexane | 0.33427 | 0.016713 | 0.055281 | 0.084666 | 0.0042333 | 0.11951 | 0.0059755 | 0.35066 | 0.017533 | 0.0061585 | 0.00030793
Cresols (total) | 0 | 0 | 0 | 0 | 0 | 0.0016026 | 8.0131e-05 | 0.00030777 | 1.5388e-05 | 0.0016668 | 8.3338e-05
Xylenes | 0.22908 | 0.011454 | 0.040254 | 0.057618 | 0.0028809 | 0.087954 | 0.0043977 | 0.25689 | 0.012845 | 0.0049563 | 0.00024782
Methyl tert-butyl ether | 0.14553 | 0.0072764 | 0.028318 | 0.036133 | 0.0018067 | 0.062889 | 0.0031444 | 0.18241 | 0.0091207 | 0.0040015 | 0.00020007
Biphenyl, 1,1- | 0.12157 | 0.0060787 | 0.024896 | 0.029974 | 0.0014987 | 0.055702 | 0.0027851 | 0.16106 | 0.0080531 | 0.0037277 | 0.00018639
Carbonyl sulfide | 0.30248 | 0.015124 | 0.050741 | 0.076493 | 0.0038247 | 0.10998 | 0.0054988 | 0.32233 | 0.016116 | 0.0057953 | 0.00028976
Dichloroethane, 1,2- | 0.17791 | 0.0088953 | 0.032944 | 0.044458 | 0.0022229 | 0.072602 | 0.0036301 | 0.21128 | 0.010564 | 0.0043715 | 0.00021857
Diethanolamine | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Trimethylpentane, 2,2,4- | 0.4467 | 0.022335 | 0.071343 | 0.11358 | 0.0056789 | 0.15324 | 0.007662 | 0.45089 | 0.022544 | 0.0074434 | 0.00037217
Compound A | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM!
Compound B | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM!
Compound C | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM!
n-Butane (VOC Surrogate) | 0.4061 | 0.020305 | 0.065544 | 0.10314 | 0.0051569 | 0.14106 | 0.0070531 | 0.4147 | 0.020735 | 0.0069795 | 0.00034897

## Weir
This sheet is used for uncovered primary weirs and uncovered weirs of oil-water separators. Directions: 1) fill-in the input data (yellow boxes); review default variables and constant (yellow boxes) and change if necessary; 2) record air emissions (green boxes); and 3) record effluent concentrations (light blue boxes) for downstream process unit emission calculations.
CRITICAL INPUTS | VALUE | UNITS | DEFAULT VARIABLES / CONSTANTS | VALUE | UNITS | DEFAULT VALUE | AIR EMISSIONS | VALUE | UNITS | EFFLUENT WATER CONCENTRATION | UNITS
Weir height, h | 1.524 | m | Diffusivity of oxygen in water, DO2,w | 2.4e-05 | cm2/s | 2.4e-05 | Methanol | 0 | g/s | 0 | g/m3
Wastewater flow rate, Q | 1 | m3/s | Universal gas constant (R ) | 8.21e-05 | atm-m3/gmol-K | 8.21e-05 | Benzene | 0 | g/s | 0 | g/m3
Length of weir, l | 3 | m | Fraction of volume that is oil (FO) | 0.001 | dimensionless | 0.001 | Carbon disulfide | 0 | g/s | 0 | g/m3
Tail water depth, z | 0.1 | m |  |  |  |  | Methyl ethyl ketone | 0 | g/s | 0 | g/m3
Temperature (T) | 25 | deg. C |  |  |  |  | Naphthalene | 0 | g/s | 0 | g/m3
[7 empty] | Cumene | 0 | g/s | 0 | g/m3
[7 empty] | Ethylbenzene | 0 | g/s | 0 | g/m3
[7 empty] | Styrene | 0 | g/s | 0 | g/m3
[7 empty] | 1,3-Butadiene | 0 | g/s | 0 | g/m3
[7 empty] | Ethylene glycol | 0 | g/s | 0 | g/m3
[7 empty] | Methyl isobutyl ketone | 0 | g/s | 0 | g/m3
[7 empty] | Toluene | 0 | g/s | 0 | g/m3
[7 empty] | Phenol | 0 | g/s | 0 | g/m3
[7 empty] | n-Hexane | 0 | g/s | 0 | g/m3
[7 empty] | Cresols (total) | 0 | g/s | 0 | g/m3
CONSTITUENT INFLUENT CONCENTRATIONS (C0) | [6 empty] | Xylenes | 0 | g/s | 0 | g/m3
Methanol | 0 | g/m3 |  |  |  |  | Methyl tert-butyl ether | 0 | g/s | 0 | g/m3
Benzene | 0 | g/m3 |  |  |  |  | Biphenyl, 1,1- | 0 | g/s | 0 | g/m3
Carbon disulfide | 0 | g/m3 |  |  |  |  | Carbonyl sulfide | 0 | g/s | 0 | g/m3
Methyl ethyl ketone | 0 | g/m3 |  |  |  |  | Dichloroethane, 1,2- | 0 | g/s | 0 | g/m3
Naphthalene | 0 | g/m3 |  |  |  |  | Diethanolamine | 0 | g/s | 0 | g/m3
Cumene | 0 | g/m3 |  |  |  |  | Trimethylpentane, 2,2,4- | 0 | g/s | 0 | g/m3
Ethylbenzene | 0 | g/m3 |  |  |  |  | Compound A | #DIV/0! | g/s | #DIV/0! | g/m3
Styrene | 0 | g/m3 |  |  |  |  | Compound B | #DIV/0! | g/s | #DIV/0! | g/m3
1,3-Butadiene | 0 | g/m3 |  |  |  |  | Compound C | #DIV/0! | g/s | #DIV/0! | g/m3
Ethylene glycol | 0 | g/m3 |  |  |  |  | n-Butane (VOC Surrogate) | 0 | g/s | 0 | g/m3
Methyl isobutyl ketone | 0 | g/m3
Toluene | 0 | g/m3
Phenol | 0 | g/m3
n-Hexane | 0 | g/m3
Cresols (total) | 0 | g/m3
Xylenes | 0 | g/m3
Methyl tert-butyl ether | 0 | g/m3
Biphenyl, 1,1- | 0 | g/m3
Carbonyl sulfide | 0 | g/m3
Dichloroethane, 1,2- | 0 | g/m3
Diethanolamine | 0 | g/m3 | [5 empty] | q | 1200
Trimethylpentane, 2,2,4- | 0 | g/m3 | [5 empty] | ln( r) | 0.31181 | (Nakasone)
Compound A | 0 | g/m3 | [5 empty] | ln( r)* | 2.2393 | (Pincince)
Compound B | 0 | g/m3
Compound C | 0 | g/m3
n-Butane (VOC Surrogate) | 0 | g/m3
[7 empty] | INTERMEDIATE OUTPUTS | Keq | kl | kg | Ko | fair | kl Pincince | Ko Pincince | fair Pincince | Emissions, Pincince
[7 empty] | Methanol | 0.00018588 | 0.053045 | 0.071094 | 1.3212e-05 | 6.0402e-05 | 0.38095 | 1.3214e-05 | 6.0415e-05 | 0
[7 empty] | Benzene | 0.22793 | 0.037762 | 0.05 | 0.0087544 | 0.039235 | 0.27119 | 0.010937 | 0.048774 | 0
[7 empty] | Carbon disulfide | 1.2347 | 0.038269 | 0.055828 | 0.024608 | 0.10641 | 0.27483 | 0.05511 | 0.22273 | 0
[7 empty] | Methyl ethyl ketone | 0.0022837 | 0.037762 | 0.047261 | 0.00010762 | 0.00049192 | 0.27119 | 0.00010789 | 0.00049313 | 0
[7 empty] | Naphthalene | 0.019732 | 0.031651 | 0.038404 | 0.00074006 | 0.0033778 | 0.22731 | 0.00075526 | 0.0034471 | 0
[7 empty] | Cumene | 0.59645 | 0.030527 | 0.049247 | 0.014969 | 0.066151 | 0.21923 | 0.025903 | 0.11168 | 0
[7 empty] | Ethylbenzene | 0.32192 | 0.032481 | 0.044994 | 0.010017 | 0.044766 | 0.23327 | 0.013638 | 0.060447 | 0
[7 empty] | Styrene | 0.11235 | 0.033028 | 0.043395 | 0.0042482 | 0.019235 | 0.2372 | 0.0047771 | 0.021604 | 0
[7 empty] | 1,3-Butadiene | 3.0068 | 0.040263 | 0.099335 | 0.03548 | 0.14974 | 0.28915 | 0.14692 | 0.48917 | 0
[7 empty] | Ethylene glycol | 7.3536e-08 | 0.04801 | 0.071911 | 5.288e-09 | 2.4177e-08 | 0.34479 | 5.288e-09 | 2.4177e-08 | 0
[7 empty] | Methyl isobutyl ketone | 0.005639 | 0.032481 | 0.044994 | 0.00025175 | 0.0011504 | 0.23327 | 0.00025344 | 0.0011581 | 0
[7 empty] | Toluene | 0.27126 | 0.034643 | 0.049624 | 0.0096943 | 0.043355 | 0.24879 | 0.01277 | 0.056714 | 0
[7 empty] | Phenol | 1.6219e-05 | 0.03596 | 0.047723 | 7.7398e-07 | 3.5386e-06 | 0.25825 | 7.74e-07 | 3.5387e-06 | 0
[7 empty] | n-Hexane | 4.984 | 0.032399 | 0.085959 | 0.030121 | 0.12865 | 0.23267 | 0.15078 | 0.49812 | 0
[7 empty] | Cresols (total) | 6.6182e-05 | 0.036479 | 0.042747 | 2.8289e-06 | 1.2933e-05 | 0.26198 | 2.8291e-06 | 1.2934e-05 | 0
[7 empty] | Xylenes | 0.2468 | 0.036583 | 0.043556 | 0.0083084 | 0.037274 | 0.26272 | 0.010327 | 0.046119 | 0
[7 empty] | Methyl tert-butyl ether | 0.022678 | 0.039522 | 0.05526 | 0.0012147 | 0.0055382 | 0.28383 | 0.0012477 | 0.0056882 | 0
[7 empty] | Biphenyl, 1,1- | 0.011439 | 0.033571 | 0.02991 | 0.00033869 | 0.0015473 | 0.24109 | 0.00034165 | 0.0015608 | 0
[7 empty] | Carbonyl sulfide | 2.01 | 0.045504 | 0.074707 | 0.034921 | 0.14757 | 0.32679 | 0.10288 | 0.37524 | 0
[7 empty] | Dichloroethane, 1,2- | 0.057194 | 0.038016 | 0.055828 | 0.0029456 | 0.013377 | 0.27302 | 0.0031561 | 0.014326 | 0
[7 empty] | Diethanolamine | 1.581e-09 | 0.037762 | 0.043153 | 6.8225e-11 | 3.1192e-10 | 0.27119 | 6.8225e-11 | 3.1192e-10 | 0
[7 empty] | Trimethylpentane, 2,2,4- | 123.784 | 0.029061 | 0.044318 | 0.028908 | 0.12381 | 0.20871 | 0.20106 | 0.60117 | 0
[7 empty] | Compound A | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | Compound B | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | Compound C | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | n-Butane (VOC Surrogate) | 38.8102 | 0.039023 | 0.054114 | 0.038311 | 0.16068 | 0.28025 | 0.24725 | 0.67711 | 0
[7 empty] | Pollutant | Influent load, g/s | Effluent load, g/s | Air emission load, g/s | % Load with effluent | % Load air emitted | Mass balance check
[7 empty] | Methanol | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | Benzene | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | Carbon disulfide | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | Methyl ethyl ketone | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | Naphthalene | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | Cumene | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | Ethylbenzene | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | Styrene | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | 1,3-Butadiene | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | Ethylene glycol | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | Methyl isobutyl ketone | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | Toluene | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | Phenol | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | n-Hexane | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | Cresols (total) | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | Xylenes | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | Methyl tert-butyl ether | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | Biphenyl, 1,1- | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | Carbonyl sulfide | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | Dichloroethane, 1,2- | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | Diethanolamine | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | Trimethylpentane, 2,2,4- | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | Compound A | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | Compound B | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | Compound C | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | n-Butane (VOC Surrogate) | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!

## Oil-Water Separators
This sheet is used for uncovered oil-water separators only. Directions: 1) fill-in the input data (yellow boxes); review default variables and constant (yellow boxes) and change if necessary; 2) record air emissions (green boxes); and 3) record effluent concentrations (light blue boxes) for downstream process unit emission calculations.
CRITICAL INPUTS | VALUE | UNITS | DEFAULT VARIABLES / CONSTANTS | VALUE | UNITS | DEFAULT VALUE | UNCONTROLLED AIR EMISSIONS | VALUE | UNITS | EFFLUENT WATER CONCENTRATION | UNITS
Surface area (A) | 200 | m2 | Viscosity of air (ma) | 0.000181 | g/cm-s | 0.000181 | Methanol | 0.00016115 | g/s | 1.0008 | g/m3
Total pressure (Po) | 1 | atm | Density of air (ρa) | 0.0012 | g/cm3 | 0.0012 | Benzene | 0.08498 | g/s | 0.88191 | g/m3
Wastewater flow rate (Q) | 1 | m3/s | Molecular weight of oil (MWoil) | 282 | g/g-mol | 282 | Carbon disulfide | 0.083126 | g/s | 0.90992 | g/m3
Windspeed (U10) | 4.413 | m/s | Molecular weight of air (MWair) | 29 | g/g-mol | 29 | Methyl ethyl ketone | 0.0013386 | g/s | 0.9991 | g/m3
|  |  | Density of oil (ρoil) | 0.92 | g/cm3 | 0.92 | Naphthalene | 0.0011897 | g/s | 0.30396 | g/m3
|  |  | Flow of oil (Qoil) [default = 0.001*Q] | 0.001 | m3/s | 0.001 | Cumene | 0 | g/s | 0 | g/m3
|  |  | Fraction of volume that is oil (FO) | 0.001 | dimensionless | 0.001 | Ethylbenzene | 0 | g/s | 0 | g/m3
CONSTITUENT INFLUENT CONCENTRATIONS (C0) |  |  | Oil layer thickness (Olayer) | 1 | cm | 1 | Styrene | 0 | g/s | 0 | g/m3
Methanol | 1 | g/m3 |  |  |  |  | 1,3-Butadiene | 0 | g/s | 0 | g/m3
Benzene | 1 | g/m3 |  |  |  |  | Ethylene glycol | 0 | g/s | 0 | g/m3
Carbon disulfide | 1 | g/m3 |  |  |  |  | Methyl isobutyl ketone | 0 | g/s | 0 | g/m3
Methyl ethyl ketone | 1 | g/m3 |  |  |  |  | Toluene | 0 | g/s | 0 | g/m3
Naphthalene | 1 | g/m3 |  |  |  |  | Phenol | 0 | g/s | 0 | g/m3
Cumene | 0 | g/m3 |  |  |  |  | n-Hexane | 0 | g/s | 0 | g/m3
Ethylbenzene | 0 | g/m3 |  |  |  |  | Cresols (total) | 0 | g/s | 0 | g/m3
Styrene | 0 | g/m3 |  |  |  |  | Xylenes | 0 | g/s | 0 | g/m3
1,3-Butadiene | 0 | g/m3 |  |  |  |  | Methyl tert-butyl ether | 0 | g/s | 0 | g/m3
Ethylene glycol | 0 | g/m3 |  |  |  |  | Biphenyl, 1,1- | 0 | g/s | 0 | g/m3
Methyl isobutyl ketone | 0 | g/m3 |  |  |  |  | Carbonyl sulfide | 0 | g/s | 0 | g/m3
Toluene | 0 | g/m3 |  |  |  |  | Dichloroethane, 1,2- | 0 | g/s | 0 | g/m3
Phenol | 0 | g/m3 |  |  |  |  | Diethanolamine | 0 | g/s | 0 | g/m3
n-Hexane | 0 | g/m3 |  |  |  |  | Trimethylpentane, 2,2,4- | 0 | g/s | 0 | g/m3
Cresols (total) | 0 | g/m3 |  |  |  |  | Compound A | #DIV/0! | g/s | #DIV/0! | g/m3
Xylenes | 0 | g/m3 |  |  |  |  | Compound B | #DIV/0! | g/s | #DIV/0! | g/m3
Methyl tert-butyl ether | 0 | g/m3 |  |  |  |  | Compound C | #DIV/0! | g/s | #DIV/0! | g/m3
Biphenyl, 1,1- | 0 | g/m3 |  |  |  |  | n-Butane (VOC Surrogate) | 0 | g/s | 0 | g/m3
Carbonyl sulfide | 0 | g/m3
Dichloroethane, 1,2- | 0 | g/m3
Diethanolamine | 0 | g/m3
Trimethylpentane, 2,2,4- | 0 | g/m3
Compound A | 0 | g/m3
Compound B | 0 | g/m3 |  |  |  |  | Windspeed (U10) | 4.413 | m/s
Compound C | 0 | g/m3
n-Butane (VOC Surrogate) | 0 | g/m3
[7 empty] | INTERMEDIATE OUTPUTS | ScG | kg,q, m/s | Keqoil | Koil, m/s | Cooil, g/m3 | CL,oil , g/m3
[7 empty] | Methanol | 1.0056 | 0.011272 | 0.0021028 | 2.3702e-05 | 0.19514 | 0.033994
[7 empty] | Benzene | 1.714 | 0.0078852 | 0.0015855 | 1.2502e-05 | 118.967 | 33.9875
[7 empty] | Carbon disulfide | 1.4503 | 0.008819 | 0.0059914 | 5.2838e-05 | 90.9918 | 7.8661
[7 empty] | Methyl ethyl ketone | 1.8667 | 0.0074469 | 0.0015905 | 1.1844e-05 | 1.9037 | 0.56511
[7 empty] | Naphthalene | 2.5565 | 0.0060322 | 1.4186e-06 | 8.5571e-09 | 696.3404 | 695.1507
[7 empty] | Cumene | 1.7539 | 0.0077646 | 7.5101e-05 | 5.8313e-07 | 0 | 0
[7 empty] | Ethylbenzene | 2.0111 | 0.0070843 | 0.00016021 | 1.135e-06 | 0 | 0
[7 empty] | Styrene | 2.1244 | 0.0068289 | 0.00010214 | 6.9748e-07 | 0 | 0
[7 empty] | 1,3-Butadiene | 0.60576 | 0.015829 | 0.035214 | 0.00055741 | 0 | 0
[7 empty] | Ethylene glycol | 0.9883 | 0.011403 | 2.1028e-06 | 2.3979e-08 | 0 | 0
[7 empty] | Methyl isobutyl ketone | 2.0111 | 0.0070843 | 0.00033211 | 2.3528e-06 | 0 | 0
[7 empty] | Toluene | 1.7337 | 0.007825 | 0.00047397 | 3.7088e-06 | 0 | 0
[7 empty] | Phenol | 1.8394 | 0.0075208 | 4.6062e-06 | 3.4642e-08 | 0 | 0
[7 empty] | n-Hexane | 0.75417 | 0.013668 | 0.00252 | 3.4443e-05 | 0 | 0
[7 empty] | Cresols (total) | 2.1734 | 0.0067254 | 5.0067e-06 | 3.3672e-08 | 0 | 0
[7 empty] | Xylenes | 2.1125 | 0.0068546 | 0.00013421 | 9.1996e-07 | 0 | 0
[7 empty] | Methyl tert-butyl ether | 1.473 | 0.0087279 | 0.0031033 | 2.7085e-05 | 0 | 0
[7 empty] | Biphenyl, 1,1- | 3.7335 | 0.0046804 | 1.6088e-07 | 7.5299e-10 | 0 | 0
[7 empty] | Carbonyl sulfide | 0.9328 | 0.011853 | 0.15708 | 0.0018619 | 0 | 0
[7 empty] | Dichloroethane, 1,2- | 1.4503 | 0.008819 | 0.0013268 | 1.1701e-05 | 0 | 0
[7 empty] | Diethanolamine | 2.1425 | 0.0067902 | 4.6395e-09 | 3.1503e-11 | 0 | 0
[7 empty] | Trimethylpentane, 2,2,4- | 2.0578 | 0.0069763 | 0.00082063 | 5.725e-06 | 0 | 0
[7 empty] | Compound A | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0!
[7 empty] | Compound B | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0!
[7 empty] | Compound C | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0!
[7 empty] | n-Butane (VOC Surrogate) | 1.5205 | 0.0085442 | 0.030374 | 0.00025952 | 0 | 0
QUALITY CONTROL CHECKS
[7 empty] | Pollutant | Influent load, g/s | Effluent load, g/s | Air emission load, g/s | % Load with effluent | % Load air emitted
[7 empty] | Methanol | 1 | 1.0008 | 0.00016115 | 100.0806 | 0.016115
[7 empty] | Benzene | 1 | 0.88191 | 0.08498 | 88.1915 | 8.498
[7 empty] | Carbon disulfide | 1 | 0.90992 | 0.083126 | 90.9918 | 8.3126
[7 empty] | Methyl ethyl ketone | 1 | 0.9991 | 0.0013386 | 99.9095 | 0.13386
[7 empty] | Naphthalene | 1 | 0.30396 | 0.0011897 | 30.3964 | 0.11897
[7 empty] | Cumene | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[7 empty] | Ethylbenzene | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[7 empty] | Styrene | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[7 empty] | 1,3-Butadiene | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[7 empty] | Ethylene glycol | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[7 empty] | Methyl isobutyl ketone | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[7 empty] | Toluene | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[7 empty] | Phenol | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[7 empty] | n-Hexane | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[7 empty] | Cresols (total) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[7 empty] | Xylenes | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[7 empty] | Methyl tert-butyl ether | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[7 empty] | Biphenyl, 1,1- | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[7 empty] | Carbonyl sulfide | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[7 empty] | Dichloroethane, 1,2- | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[7 empty] | Diethanolamine | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[7 empty] | Trimethylpentane, 2,2,4- | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[7 empty] | Compound A | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | Compound B | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | Compound C | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | n-Butane (VOC Surrogate) | 0 | 0 | 0 | #DIV/0! | #DIV/0!

## DAF
This sheet is used for uncovered dissolved air floatation (DAF) units only. Directions: 1) fill-in the input data (yellow boxes); review default variables and constant (yellow boxes) and change if necessary; 2) record air emissions (green boxes); and 3) record effluent concentrations (light blue boxes) for downstream process unit emission calculations.
CRITICAL INPUTS | VALUE | UNITS | DEFAULT VARIABLES / CONSTANTS | VALUE | UNITS | DEFAULT VALUE | AIR EMISSIONS | VALUE | UNITS | EFFLUENT WATER CONCENTRATION | UNITS
Surface area (A) | 200 | m2 | Viscosity of water (mL) | 0.00893 | g/cm-s | 0.00893 | Methanol | 0.00054363 | g/s | 0.97282 | g/m3
Temperature (T) | 0.5 | deg. C | Density of water (ρL) | 1 | g/cm3 | 1 | Benzene | 0.018516 | g/s | 0.074175 | g/m3
Total pressure (Po) | 1 | atm | Universal gas constant (R ) | 8.21e-05 | atm-m3/gmol-K | 8.21e-05 | Carbon disulfide | 0.019707 | g/s | 0.014635 | g/m3
Wastewater flow rate (Q) | 0.02 | m3/s | Viscosity of air (ma) | 0.000181 | g/cm-s | 0.000181 | Methyl ethyl ketone | 0.0029427 | g/s | 0.85287 | g/m3
Wastewater depth (D) | 3 | m | Density of air (ρa) | 0.0012 | g/cm3 | 0.0012 | Naphthalene | 0.010613 | g/s | 0.46937 | g/m3
Diffused air flow rate (Qa) | 1 | m3/s | Diffusivity of ether in water (Dether) | 8.5e-06 | cm2/sec | 8.5e-06 | Cumene | 0.019404 | g/s | 0.029807 | g/m3
Windspeed (U10) | 4.413 | m/s |  |  |  |  | Ethylbenzene | 0.018925 | g/s | 0.053775 | g/m3
[7 empty] | Styrene | 0 | g/s | 0 | g/m3
CONSTITUENT INFLUENT CONCENTRATIONS (C0) | [6 empty] | 1,3-Butadiene | 0 | g/s | 0 | g/m3
Methanol | 1 | g/m3 |  |  |  |  | Ethylene glycol | 0 | g/s | 0 | g/m3
Benzene | 1 | g/m3 |  |  |  |  | Methyl isobutyl ketone | 0 | g/s | 0 | g/m3
Carbon disulfide | 1 | g/m3 |  |  |  |  | Toluene | 0 | g/s | 0 | g/m3
Methyl ethyl ketone | 1 | g/m3 |  |  |  |  | Phenol | 0 | g/s | 0 | g/m3
Naphthalene | 1 | g/m3 |  |  |  |  | n-Hexane | 0 | g/s | 0 | g/m3
Cumene | 1 | g/m3 |  |  |  |  | Cresols (total) | 0 | g/s | 0 | g/m3
Ethylbenzene | 1 | g/m3 |  |  |  |  | Xylenes | 0 | g/s | 0 | g/m3
Styrene | 0 | g/m3 |  |  |  |  | Methyl tert-butyl ether | 0 | g/s | 0 | g/m3
1,3-Butadiene | 0 | g/m3 |  |  |  |  | Biphenyl, 1,1- | 0 | g/s | 0 | g/m3
Ethylene glycol | 0 | g/m3 |  |  |  |  | Carbonyl sulfide | 0 | g/s | 0 | g/m3
Methyl isobutyl ketone | 0 | g/m3 |  |  |  |  | Dichloroethane, 1,2- | 0 | g/s | 0 | g/m3
Toluene | 0 | g/m3 |  |  |  |  | Diethanolamine | 0 | g/s | 0 | g/m3
Phenol | 0 | g/m3 |  |  |  |  | Trimethylpentane, 2,2,4- | 0 | g/s | 0 | g/m3
n-Hexane | 0 | g/m3 |  |  |  |  | Compound A | #DIV/0! | g/s | #DIV/0! | g/m3
Cresols (total) | 0 | g/m3 |  |  |  |  | Compound B | #DIV/0! | g/s | #DIV/0! | g/m3
Xylenes | 0 | g/m3 |  |  |  |  | Compound C | #DIV/0! | g/s | #DIV/0! | g/m3
Methyl tert-butyl ether | 0 | g/m3 |  |  |  |  | n-Butane (VOC Surrogate) | 0 | g/s | 0 | g/m3
Biphenyl, 1,1- | 0 | g/m3
Carbonyl sulfide | 0 | g/m3
Dichloroethane, 1,2- | 0 | g/m3
Diethanolamine | 0 | g/m3
Trimethylpentane, 2,2,4- | 0 | g/m3
Compound A | 0 | g/m3
Compound B | 0 | g/m3
Compound C | 0 | g/m3
n-Butane (VOC Surrogate) | 0 | g/m3
[10 empty] | Windspeed (U10) | 4.413 | m/s
[10 empty] | INTERMEDIATE OUTPUTS | ScL | ScG | kl,q | kg,q | Keq | KOL
[10 empty] | Methanol | 544.5122 | 1.0056 | 8.1128e-06 | 0.011272 | 0.00020252 | 1.7815e-06
[10 empty] | Benzene | 911.2245 | 1.714 | 6.4983e-06 | 0.0078852 | 0.24834 | 6.4768e-06
[10 empty] | Carbon disulfide | 893 | 1.4503 | 6.5541e-06 | 0.008819 | 1.3453 | 6.5505e-06
[10 empty] | Methyl ethyl ketone | 911.2245 | 1.8667 | 6.4983e-06 | 0.0074469 | 0.0024881 | 4.811e-06
[10 empty] | Naphthalene | 1190.6667 | 2.5565 | 5.81e-06 | 0.0060322 | 0.021499 | 5.5609e-06
[10 empty] | Cumene | 1257.7465 | 1.7539 | 5.68e-06 | 0.0077646 | 0.64985 | 5.6736e-06
[10 empty] | Ethylbenzene | 1144.8718 | 2.0111 | 5.9053e-06 | 0.0070843 | 0.35074 | 5.8913e-06
[10 empty] | Styrene | 1116.25 | 2.1244 | 5.9678e-06 | 0.0068289 | 0.1224 | 5.9255e-06
[10 empty] | 1,3-Butadiene | 826.8519 | 0.60576 | 6.772e-06 | 0.015829 | 3.276 | 6.7711e-06
[10 empty] | Ethylene glycol | 633.3333 | 0.9883 | 7.5952e-06 | 0.011403 | 8.012e-08 | 9.1351e-10
[10 empty] | Methyl isobutyl ketone | 1144.8718 | 2.0111 | 5.9053e-06 | 0.0070843 | 0.0061439 | 5.1998e-06
[10 empty] | Toluene | 1038.3721 | 1.7337 | 6.1507e-06 | 0.007825 | 0.29555 | 6.1344e-06
[10 empty] | Phenol | 981.3187 | 1.8394 | 6.2983e-06 | 0.0075208 | 1.7671e-05 | 1.3015e-07
[10 empty] | n-Hexane | 1149.2921 | 0.75417 | 5.8958e-06 | 0.013668 | 5.4303 | 5.8954e-06
[10 empty] | Cresols (total) | 960.2151 | 2.1734 | 6.3562e-06 | 0.0067254 | 7.2107e-05 | 4.5057e-07
[10 empty] | Xylenes | 956.1028 | 2.1125 | 6.3677e-06 | 0.0068546 | 0.2689 | 6.3458e-06
[10 empty] | Methyl tert-butyl ether | 850.4762 | 1.473 | 6.6913e-06 | 0.0087279 | 0.024709 | 6.4899e-06
[10 empty] | Biphenyl, 1,1- | 1089.0244 | 3.7335 | 6.0295e-06 | 0.0046804 | 0.012463 | 5.4646e-06
[10 empty] | Carbonyl sulfide | 686.9231 | 0.9328 | 7.3327e-06 | 0.011853 | 2.1899 | 7.3306e-06
[10 empty] | Dichloroethane, 1,2- | 902.0202 | 1.4503 | 6.5263e-06 | 0.008819 | 0.062315 | 6.4497e-06
[10 empty] | Diethanolamine | 911.2245 | 2.1425 | 6.4983e-06 | 0.0067902 | 1.7226e-09 | 1.1696e-11
[10 empty] | Trimethylpentane, 2,2,4- | 1355.0835 | 2.0578 | 5.5088e-06 | 0.0069763 | 134.8665 | 5.5087e-06
[10 empty] | Compound A | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0!
[10 empty] | Compound B | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0!
[10 empty] | Compound C | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0!
[10 empty] | n-Butane (VOC Surrogate) | 866.9903 | 1.5205 | 6.6368e-06 | 0.0085442 | 42.2849 | 6.6367e-06
Parameters for kl,q calculation
[10 empty] | U* | 0.13151 | m/s
[10 empty] | F/D | 5.3192
QUALITY CONTROL CHECKS
[10 empty] | Pollutant | Influent load, g/s | Effluent load, g/s | Air emission load, g/s | % Load with effluent | % Load air emitted
[10 empty] | Methanol | 0.02 | 0.019456 | 0.00054363 | 97.2818 | 2.7182
[10 empty] | Benzene | 0.02 | 0.0014835 | 0.018516 | 7.4175 | 92.5825
[10 empty] | Carbon disulfide | 0.02 | 0.0002927 | 0.019707 | 1.4635 | 98.5365
[10 empty] | Methyl ethyl ketone | 0.02 | 0.017057 | 0.0029427 | 85.2866 | 14.7134
[10 empty] | Naphthalene | 0.02 | 0.0093873 | 0.010613 | 46.9366 | 53.0634
[10 empty] | Cumene | 0.02 | 0.00059614 | 0.019404 | 2.9807 | 97.0193
[10 empty] | Ethylbenzene | 0.02 | 0.0010755 | 0.018925 | 5.3775 | 94.6225
[10 empty] | Styrene | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | 1,3-Butadiene | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | Ethylene glycol | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | Methyl isobutyl ketone | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | Toluene | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | Phenol | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | n-Hexane | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | Cresols (total) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | Xylenes | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | Methyl tert-butyl ether | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | Biphenyl, 1,1- | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | Carbonyl sulfide | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | Dichloroethane, 1,2- | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | Diethanolamine | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | Trimethylpentane, 2,2,4- | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | Compound A | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | Compound B | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | Compound C | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | n-Butane (VOC Surrogate) | 0 | 0 | 0 | #DIV/0! | #DIV/0!

## EQ Tanks
This sheet is used for uncovered equalization tanks only. Directions: 1) fill-in the input data (yellow boxes); review default variables and constant (yellow boxes) and change if necessary; 2) record air emissions (green boxes); and 3) record effluent concentrations (light blue boxes) for downstream process unit emission calculations.
CRITICAL INPUTS | VALUE | UNITS | DEFAULT VARIABLES / CONSTANTS | VALUE | UNITS | DEFAULT VALUE | AIR EMISSIONS | VALUE | UNITS | EFFLUENT WATER CONCENTRATION | UNITS
Surface area (A) | 50000 | m2 | Viscosity of water (mL) | 0.00893 | g/cm-s | 0.00893 | Methanol | 0.081088 | g/s | 0.082814 | g/m3
Temperature (T) | 19 | deg. C | Density of water (ρL) | 1 | g/cm3 | 1 | Benzene | 0.084891 | g/s | 0.039801 | g/m3
Total pressure (Po) | 1 | atm | Universal gas constant (R ) | 8.21e-05 | atm-m3/gmol-K | 8.21e-05 | Carbon disulfide | 0.084931 | g/s | 0.039354 | g/m3
Wastewater flow rate (Q) | 0.08841 | m3/s | Viscosity of air (ma) | 0.000181 | g/cm-s | 0.000181 | Methyl ethyl ketone | 0.084185 | g/s | 0.047783 | g/m3
Wastewater depth (D) | 5 | m | Density of air (ρa) | 0.0012 | g/cm3 | 0.0012 | Naphthalene | 0.084306 | g/s | 0.046426 | g/m3
Total power to aerators (Ptot) | 100 | hp | Quiescent surface area (AQ) [default=A-AT] | 0 | m2 | 0 | Cumene | 0.08431 | g/s | 0.046379 | g/m3
Number of aerators (Naer) | 1 | number | Oxygen transfer correction factor (Ot) | 0.83 | dimensionless | 0.83 | Ethylbenzene | 0.084487 | g/s | 0.044378 | g/m3
Windspeed (U10) | 4.47 | m/s | Oxygen transfer rating to surface area (J) | 3 | lb O2/hp-hr | 3 | Styrene | 0.084523 | g/s | 0.043969 | g/m3
Turbulent surface area (AT) | 50000 | m2 | Impeller diameter (d) | 61 | cm | 61 | 1,3-Butadiene | 0.085058 | g/s | 0.037916 | g/m3
|  |  | Impeller diameter (d*) | 2.0008 | ft | 2.0008 | Ethylene glycol | 0 | g/s | 0 | g/m3
|  |  | Rotational speed of impeller (w) | 126 | rad/s | 126 | Methyl isobutyl ketone | 0 | g/s | 0 | g/m3
CONSTITUENT INFLUENT CONCENTRATIONS (C0) |  |  | Diffusivity of ether in water (Dether) | 8.5e-06 | cm2/sec | 8.5e-06 | Toluene | 0 | g/s | 0 | g/m3
Methanol | 1 | g/m3 |  |  |  |  | Phenol | 0 | g/s | 0 | g/m3
Benzene | 1 | g/m3 |  |  |  |  | n-Hexane | 0 | g/s | 0 | g/m3
Carbon disulfide | 1 | g/m3 |  |  |  |  | Cresols (total) | 0 | g/s | 0 | g/m3
Methyl ethyl ketone | 1 | g/m3 |  |  |  |  | Xylenes | 0 | g/s | 0 | g/m3
Naphthalene | 1 | g/m3 |  |  |  |  | Methyl tert-butyl ether | 0 | g/s | 0 | g/m3
Cumene | 1 | g/m3 |  |  |  |  | Biphenyl, 1,1- | 0 | g/s | 0 | g/m3
Ethylbenzene | 1 | g/m3 |  |  |  |  | Carbonyl sulfide | 0 | g/s | 0 | g/m3
Styrene | 1 | g/m3 |  |  |  |  | Dichloroethane, 1,2- | 0 | g/s | 0 | g/m3
1,3-Butadiene | 1 | g/m3 |  |  |  |  | Diethanolamine | 0 | g/s | 0 | g/m3
Ethylene glycol | 0 | g/m3 |  |  |  |  | Trimethylpentane, 2,2,4- | 0 | g/s | 0 | g/m3
Methyl isobutyl ketone | 0 | g/m3 |  |  |  |  | Compound A | #DIV/0! | g/s | #DIV/0! | g/m3
Toluene | 0 | g/m3 |  |  |  |  | Compound B | #DIV/0! | g/s | #DIV/0! | g/m3
Phenol | 0 | g/m3 |  |  |  |  | Compound C | #DIV/0! | g/s | #DIV/0! | g/m3
n-Hexane | 0 | g/m3 |  |  |  |  | n-Butane (VOC Surrogate) | 0 | g/s | 0 | g/m3
Cresols (total) | 0 | g/m3
Xylenes | 0 | g/m3
Methyl tert-butyl ether | 0 | g/m3
Biphenyl, 1,1- | 0 | g/m3
Carbonyl sulfide | 0 | g/m3 | [18 empty] | 495.95
Dichloroethane, 1,2- | 0 | g/m3 | [18 empty] | 282.625
Diethanolamine | 0 | g/m3 | [18 empty] | 534.95
Trimethylpentane, 2,2,4- | 0 | g/m3 | [18 empty] | 267.475
Compound A | 0 | g/m3 | [18 empty] | 133.7375
Compound B | 0 | g/m3
Compound C | 0 | g/m3
n-Butane (VOC Surrogate) | 0 | g/m3
[10 empty] | Windspeed (U10) | 4.47 | m/s
[10 empty] | INTERMEDIATE OUTPUTS | ScL | ScG | kl,q | kg,q | kl,t | kg,t | Keq | KT | KQ | KOL
[10 empty] | Methanol | 544.5122 | 1.0056 | 8.0252e-06 | 0.0084033 | 5.5292e-05 | 0.15985 | 0.0001897 | 1.9583e-05 | 1.3299e-06 | 1.9583e-05
[10 empty] | Benzene | 911.2245 | 1.714 | 5.6935e-06 | 0.0058786 | 4.2741e-05 | 0.093779 | 0.23261 | 4.2658e-05 | 5.6699e-06 | 4.2658e-05
[10 empty] | Carbon disulfide | 893 | 1.4503 | 5.7707e-06 | 0.0065748 | 4.3175e-05 | 0.11083 | 1.2601 | 4.3162e-05 | 5.7667e-06 | 4.3162e-05
[10 empty] | Methyl ethyl ketone | 911.2245 | 1.8667 | 5.6935e-06 | 0.0055518 | 4.2741e-05 | 0.086106 | 0.0023306 | 3.5237e-05 | 3.9537e-06 | 3.5237e-05
[10 empty] | Naphthalene | 1190.6667 | 2.5565 | 4.7636e-06 | 0.0044972 | 3.7391e-05 | 0.062874 | 0.020137 | 3.6318e-05 | 4.5256e-06 | 3.6318e-05
[10 empty] | Cumene | 1257.7465 | 1.7539 | 4.5927e-06 | 0.0057887 | 3.638e-05 | 0.091647 | 0.6087 | 3.6357e-05 | 4.5867e-06 | 3.6357e-05
[10 empty] | Ethylbenzene | 1144.8718 | 2.0111 | 4.8898e-06 | 0.0052815 | 3.8131e-05 | 0.079925 | 0.32853 | 3.8076e-05 | 4.8761e-06 | 3.8076e-05
[10 empty] | Styrene | 1116.25 | 2.1244 | 4.973e-06 | 0.0050911 | 3.8617e-05 | 0.075662 | 0.11465 | 3.8446e-05 | 4.931e-06 | 3.8446e-05
[10 empty] | 1,3-Butadiene | 826.8519 | 0.60576 | 6.0745e-06 | 0.011801 | 4.4869e-05 | 0.26535 | 3.0685 | 4.4867e-05 | 6.0735e-06 | 4.4867e-05
[10 empty] | Ethylene glycol | 633.3333 | 0.9883 | 7.2562e-06 | 0.0085013 | 5.1268e-05 | 0.16264 | 7.5046e-08 | 1.2203e-08 | 6.3793e-10 | 1.2203e-08
[10 empty] | Methyl isobutyl ketone | 1144.8718 | 2.0111 | 4.8898e-06 | 0.0052815 | 3.8131e-05 | 0.079925 | 0.0057548 | 3.5212e-05 | 4.2122e-06 | 3.5212e-05
[10 empty] | Toluene | 1038.3721 | 1.7337 | 5.2187e-06 | 0.0058337 | 4.0039e-05 | 0.092713 | 0.27683 | 3.9977e-05 | 5.2019e-06 | 3.9977e-05
[10 empty] | Phenol | 981.3187 | 1.8394 | 5.4191e-06 | 0.0056069 | 4.1187e-05 | 0.087385 | 1.6552e-05 | 1.3973e-06 | 9.1241e-08 | 1.3973e-06
[10 empty] | n-Hexane | 1149.2921 | 0.75417 | 4.8773e-06 | 0.01019 | 3.8058e-05 | 0.21313 | 5.0864 | 3.8057e-05 | 4.8768e-06 | 3.8057e-05
[10 empty] | Cresols (total) | 960.2151 | 2.1734 | 5.4982e-06 | 0.0050139 | 4.1637e-05 | 0.073957 | 6.7541e-05 | 4.4601e-06 | 3.19e-07 | 4.4601e-06
[10 empty] | Xylenes | 956.1028 | 2.1125 | 5.5139e-06 | 0.0051103 | 4.1726e-05 | 0.076089 | 0.25187 | 4.1636e-05 | 5.4904e-06 | 4.1636e-05
[10 empty] | Methyl tert-butyl ether | 850.4762 | 1.473 | 5.9615e-06 | 0.0065068 | 4.4242e-05 | 0.10912 | 0.023144 | 4.348e-05 | 5.7345e-06 | 4.348e-05
[10 empty] | Biphenyl, 1,1- | 1089.0244 | 3.7335 | 5.0556e-06 | 0.0034893 | 3.9097e-05 | 0.043053 | 0.011674 | 3.6275e-05 | 4.4974e-06 | 3.6275e-05
[10 empty] | Carbonyl sulfide | 686.9231 | 0.9328 | 6.8737e-06 | 0.008837 | 4.9228e-05 | 0.17232 | 2.0512 | 4.9221e-05 | 6.8711e-06 | 4.9221e-05
[10 empty] | Dichloroethane, 1,2- | 902.0202 | 1.4503 | 5.7322e-06 | 0.0065748 | 4.2959e-05 | 0.11083 | 0.058369 | 4.2676e-05 | 5.6478e-06 | 4.2676e-05
[10 empty] | Diethanolamine | 911.2245 | 2.1425 | 5.6935e-06 | 0.0050622 | 4.2741e-05 | 0.075023 | 1.6135e-09 | 1.2105e-10 | 8.1678e-12 | 1.2105e-10
[10 empty] | Trimethylpentane, 2,2,4- | 1355.0835 | 2.0578 | 4.37e-06 | 0.005201 | 3.5049e-05 | 0.078113 | 126.3262 | 3.5049e-05 | 4.37e-06 | 3.5049e-05
[10 empty] | Compound A | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | Compound B | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | Compound C | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | n-Butane (VOC Surrogate) | 866.9903 | 1.5205 | 5.8856e-06 | 0.0063699 | 4.3818e-05 | 0.10571 | 39.6072 | 4.3818e-05 | 5.8854e-06 | 4.3818e-05
[10 empty] | Power number (P) | 0.00037512
[10 empty] | Reynolds number (Re) | 3108371.2707
[10 empty] | Froude number (Fr) | 987.4013
[10 empty] | Turbulent surface area (Vav), ft2 | 537900
[10 empty] | F/D | 50.4627
[10 empty] | Effective Diameter (de) | 252.3772
[10 empty] | U* | 0.13347
QUALITY CONTROL CHECKS
[10 empty] | Pollutant | Influent load, g/s | Effluent load, g/s | Air emission load, g/s | % Load with effluent | % Load air emitted
[10 empty] | Methanol | 0.08841 | 0.0073216 | 0.081088 | 8.2814 | 91.7186
[10 empty] | Benzene | 0.08841 | 0.0035188 | 0.084891 | 3.9801 | 96.0199
[10 empty] | Carbon disulfide | 0.08841 | 0.0034793 | 0.084931 | 3.9354 | 96.0646
[10 empty] | Methyl ethyl ketone | 0.08841 | 0.0042245 | 0.084185 | 4.7783 | 95.2217
[10 empty] | Naphthalene | 0.08841 | 0.0041045 | 0.084306 | 4.6426 | 95.3574
[10 empty] | Cumene | 0.08841 | 0.0041004 | 0.08431 | 4.6379 | 95.3621
[10 empty] | Ethylbenzene | 0.08841 | 0.0039234 | 0.084487 | 4.4378 | 95.5622
[10 empty] | Styrene | 0.08841 | 0.0038873 | 0.084523 | 4.3969 | 95.6031
[10 empty] | 1,3-Butadiene | 0.08841 | 0.0033521 | 0.085058 | 3.7916 | 96.2084
[10 empty] | Ethylene glycol | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | Methyl isobutyl ketone | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | Toluene | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | Phenol | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | n-Hexane | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | Cresols (total) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | Xylenes | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | Methyl tert-butyl ether | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | Biphenyl, 1,1- | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | Carbonyl sulfide | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | Dichloroethane, 1,2- | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | Diethanolamine | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | Trimethylpentane, 2,2,4- | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | Compound A | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | Compound B | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | Compound C | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | n-Butane (VOC Surrogate) | 0 | 0 | 0 | #DIV/0! | #DIV/0!

## Bio. Diff. Aer. Act. Sldg.
This sheet is used for uncovered biological treatment units with diffused aeration only. Directions: 1) fill-in the input data (yellow boxes); review default variables and constant (yellow boxes) and change if necessary; 2) record air emissions (green boxes); and 3) record effluent concentrations (light blue boxes) for downstream process unit emission calculations.
CRITICAL INPUTS | VALUE | UNITS | DEFAULT VARIABLES / CONSTANTS | VALUE | UNITS | DEFAULT VALUE | AIR EMISSIONS | VALUE | UNITS | EFFLUENT WATER CONCENTRATION | UNITS
Windspeed (U10) | 4.47 | m/s | Viscosity of water (mL) | 0.00893 | g/cm-s | 0.00893 | Methanol | 0.0008268 | g/s | 0.4127 | g/m3
Surface area (A) | 1225 | m2 | Density of water (ρL) | 1 | g/cm3 | 1 | Benzene | 0.088469 | g/s | 0.083305 | g/m3
Temperature (T) | 25 | deg. C | Universal gas constant (R ) | 8.21e-05 | atm-m3/gmol-K | 8.21e-05 | Carbon disulfide | 0.43614 | g/s | 0.076655 | g/m3
Total pressure (Po) | 1 | atm | Viscosity of air (ma) | 0.000181 | g/cm-s | 0.000181 | Methyl ethyl ketone | 0.0058981 | g/s | 0.41944 | g/m3
Wastewater flow rate (Q) | 1 | m3/s | Density of air (ρa) | 0.0012 | g/cm3 | 0.0012 | Naphthalene | 0.011671 | g/s | 0.12153 | g/m3
Wastewater depth (D) | 7 | m | Quiescent surface area (AQ) [default=A-AT] | 725 | m2 | 725 | Cumene | 0.1135 | g/s | 0.041197 | g/m3
Biological treatment unit suspended solids (CMLSS) | 3000 | g/m3 | Oxygen transfer correction factor (Ot) | 0.83 | dimensionless | 0.83 | Ethylbenzene | 0.08663 | g/s | 0.058007 | g/m3
Turbulent surface area (AT) | 500 | m2 | Oxygen transfer rating to surface area (J) | 3 | lb O2/hp-hr | 3 | Styrene | 0 | g/s | 0 | g/m3
Diffused air volumetric flow rate (Qa) | 3.51 | m3/s | Weight fraction of carbon in biomass (foc) | 0.33 | dimensionless | 0.33 | 1,3-Butadiene | 0 | g/s | 0 | g/m3
Wasted sludge volumetric flow rate (Qw) | 0.0016 | m3/s | Diffusivity of ether in water (Dether) | 8.5e-06 | cm2/sec | 8.5e-06 | Ethylene glycol | 0 | g/s | 0 | g/m3
Biological treatment unit volatile suspended solids (CMLVSS) | 1500 | g/m3 | Biomass volatile suspend solids yield from influent BOD (Y) | 0.67 | g VSS/g BOD | 0.67 | Methyl isobutyl ketone | 0 | g/s | 0 | g/m3
Influent 5-day biochemcial oxygen demand concentration (CBOD5,i) | 150 | g/m3 |  |  |  |  | Toluene | 0 | g/s | 0 | g/m3
Wasted sludge volatile suspended solids (CWAS,VSS) | 15000 | g/m3 |  |  |  |  | Phenol | 0 | g/s | 0 | g/m3
Blower gauge pressure (Pg) | 9 | lb/in2 |  |  |  |  | n-Hexane | 0 | g/s | 0 | g/m3
[7 empty] | Cresols (total) | 0 | g/s | 0 | g/m3
[7 empty] | Xylenes | 0 | g/s | 0 | g/m3
CONSTITUENT INFLUENT CONCENTRATIONS (C0) | [6 empty] | Methyl tert-butyl ether | 0 | g/s | 0 | g/m3
Methanol | 1 | g/m3 |  |  |  |  | Biphenyl, 1,1- | 0 | g/s | 0 | g/m3
Benzene | 1 | g/m3 |  |  |  |  | Carbonyl sulfide | 0 | g/s | 0 | g/m3
Carbon disulfide | 1 | g/m3 |  |  |  |  | Dichloroethane, 1,2- | 0 | g/s | 0 | g/m3
Methyl ethyl ketone | 1 | g/m3 |  |  |  |  | Diethanolamine | 0 | g/s | 0 | g/m3
Naphthalene | 1 | g/m3 |  |  |  |  | Trimethylpentane, 2,2,4- | 0 | g/s | 0 | g/m3
Cumene | 1 | g/m3 |  |  |  |  | Compound A | #DIV/0! | g/s | #DIV/0! | g/m3
Ethylbenzene | 1 | g/m3 |  |  |  |  | Compound B | #DIV/0! | g/s | #DIV/0! | g/m3
Styrene | 0 | g/m3 |  |  |  |  | Compound C | #DIV/0! | g/s | #DIV/0! | g/m3
1,3-Butadiene | 0 | g/m3 |  |  |  |  | n-Butane (VOC Surrogate) | 0 | g/s | 0 | g/m3
Ethylene glycol | 0 | g/m3
Methyl isobutyl ketone | 0 | g/m3
Toluene | 0 | g/m3
Phenol | 0 | g/m3
n-Hexane | 0 | g/m3
Cresols (total) | 0 | g/m3
Xylenes | 0 | g/m3
Methyl tert-butyl ether | 0 | g/m3
Biphenyl, 1,1- | 0 | g/m3
Carbonyl sulfide | 0 | g/m3
Dichloroethane, 1,2- | 0 | g/m3
Diethanolamine | 0 | g/m3
Trimethylpentane, 2,2,4- | 0 | g/m3
Compound A | 0 | g/m3
Compound B | 0 | g/m3 | [7 empty] | Windspeed (U10) | 4.47 | m/s
Compound C | 0 | g/m3
n-Butane (VOC Surrogate) | 0 | g/m3
[10 empty] | INTERMEDIATE OUTPUTS | ScL | ScG | kl,q | kl,t | kg,q | kg,t | KT | KQ | Keq | KOL | a | b | c | kabs | f
[10 empty] | Methanol | 544.5122 | 1.0056 | 8.349e-06 | 7.7411e-05 | 0.010305 | 0.00023223 | 4.3143e-08 | 1.558e-06 | 0.00018588 | 9.3971e-07 | 1.0004 | 217.6614 | -90 | 3.0797e-08
[10 empty] | Benzene | 911.2245 | 1.714 | 6.6809e-06 | 5.984e-05 | 0.0072089 | 0.00017952 | 2.4301e-05 | 6.6539e-06 | 0.22793 | 1.3857e-05 | 2.0609 | 162.7401 | -13.5714 | 2.1307e-05
[10 empty] | Carbon disulfide | 893 | 1.4503 | 6.7386e-06 | 6.0448e-05 | 0.0080626 | 0.00018134 | 4.7598e-05 | 6.734e-06 | 1.2347 | 2.3413e-05 | 6.6884 | 222.8492 | -17.1219 | 1.5795e-05
[10 empty] | Methyl ethyl ketone | 911.2245 | 1.8667 | 6.6809e-06 | 5.984e-05 | 0.0068082 | 0.00017952 | 4.0718e-07 | 4.6729e-06 | 0.0022837 | 2.9318e-06 | 1.0125 | 23.4164 | -10 | 3.0096e-07
[10 empty] | Naphthalene | 1190.6667 | 2.5565 | 5.9698e-06 | 5.2349e-05 | 0.0055149 | 0.00015705 | 2.9257e-06 | 5.6593e-06 | 0.019732 | 4.5435e-06 | 1.1031 | 349.3329 | -42.47 | 0.00036184
[10 empty] | Cumene | 1257.7465 | 1.7539 | 5.8354e-06 | 5.0934e-05 | 0.0070987 | 0.0001528 | 3.2674e-05 | 5.8274e-06 | 0.59645 | 1.6785e-05 | 3.768 | 261.9169 | -10.7966 | 0.0006005
[10 empty] | Ethylbenzene | 1144.8718 | 2.0111 | 6.0682e-06 | 5.3386e-05 | 0.0064767 | 0.00016016 | 2.6228e-05 | 6.0506e-06 | 0.32192 | 1.4286e-05 | 2.4971 | 55.6774 | -3.2381 | 0.00021803
[10 empty] | Styrene | 1116.25 | 2.1244 | 6.1328e-06 | 5.4066e-05 | 0.0062432 | 0.0001622 | 1.3629e-05 | 6.0796e-06 | 0.11235 | 9.1609e-06 | 1.528 | 654.2433 | 0 | 0.00013757
[10 empty] | 1,3-Butadiene | 826.8519 | 0.60576 | 6.9637e-06 | 6.2819e-05 | 0.014472 | 0.00018846 | 5.655e-05 | 6.9626e-06 | 3.0068 | 2.7202e-05 | 14.8175 | 435.9974 | 0 | 1.5435e-05
[10 empty] | Ethylene glycol | 633.3333 | 0.9883 | 7.8142e-06 | 7.1778e-05 | 0.010425 | 0.00021533 | 1.5835e-11 | 7.6655e-10 | 7.3536e-08 | 4.6013e-10 | 0.9984 | 414.7865 | 0 | 1.4405e-09
[10 empty] | Methyl isobutyl ketone | 1144.8718 | 2.0111 | 6.0682e-06 | 5.3386e-05 | 0.0064767 | 0.00016016 | 8.881e-07 | 5.2036e-06 | 0.005639 | 3.4422e-06 | 1.0285 | 6.9733 | 0 | 2.4463e-06
[10 empty] | Toluene | 1038.3721 | 1.7337 | 6.3218e-06 | 5.6057e-05 | 0.0071539 | 0.00016817 | 2.5151e-05 | 6.3012e-06 | 0.27126 | 1.3995e-05 | 2.2614 | 594.311 | 0 | 8.8821e-05
[10 empty] | Phenol | 981.3187 | 1.8394 | 6.4743e-06 | 5.7663e-05 | 0.0068757 | 0.00017299 | 2.8055e-09 | 1.0963e-07 | 1.6219e-05 | 6.6026e-08 | 0.99867 | 700.5974 | 0 | 4.77e-06
[10 empty] | n-Hexane | 1149.2921 | 0.75417 | 6.0584e-06 | 5.3283e-05 | 0.012496 | 0.00015985 | 4.9943e-05 | 6.0578e-06 | 4.984 | 2.397e-05 | 23.9164 | 358.5326 | 0 | 0.0015795
[10 empty] | Cresols (total) | 960.2151 | 2.1734 | 6.5341e-06 | 5.8294e-05 | 0.0061486 | 0.00017488 | 1.1572e-08 | 3.8307e-07 | 6.6182e-05 | 2.3144e-07 | 0.99899 | 165.7057 | 0 | 1.5795e-07
[10 empty] | Xylenes | 956.1028 | 2.1125 | 6.546e-06 | 5.8419e-05 | 0.0062667 | 0.00017526 | 2.4853e-05 | 6.5184e-06 | 0.2468 | 1.4002e-05 | 2.1527 | 340.3443 | 0 | 0.00023362
[10 empty] | Methyl tert-butyl ether | 850.4762 | 1.473 | 6.8803e-06 | 6.194e-05 | 0.0079793 | 0.00018582 | 3.9457e-06 | 6.6283e-06 | 0.022678 | 5.5334e-06 | 1.1095 | 152.817 | 0 | 1.2589e-05
[10 empty] | Biphenyl, 1,1- | 1089.0244 | 3.7335 | 6.1965e-06 | 5.4738e-05 | 0.004279 | 0.00016421 | 1.8161e-06 | 5.5002e-06 | 0.011439 | 3.9965e-06 | 1.0776 | 150.3948 | 0 | 0.0009089
[10 empty] | Carbonyl sulfide | 686.9231 | 0.9328 | 7.543e-06 | 6.8921e-05 | 0.010837 | 0.00020676 | 5.9117e-05 | 7.5404e-06 | 2.01 | 2.8592e-05 | 10.2487 | 284.8956 | 0 | 9.9865e-07
[10 empty] | Dichloroethane, 1,2- | 902.0202 | 1.4503 | 6.7098e-06 | 6.0145e-05 | 0.0080626 | 0.00018043 | 8.8084e-06 | 6.6136e-06 | 0.057194 | 7.5094e-06 | 1.2699 | 17.7267 | 0 | 4.77e-06
[10 empty] | Diethanolamine | 911.2245 | 2.1425 | 6.6809e-06 | 5.984e-05 | 0.0062078 | 0.00017952 | 2.8382e-13 | 9.8145e-12 | 1.581e-09 | 5.9245e-12 | 0.9984 | 126.534 | 0 | 5.8683e-09
[10 empty] | Trimethylpentane, 2,2,4- | 1355.0835 | 2.0578 | 5.6585e-06 | 4.9071e-05 | 0.006378 | 0.00014721 | 4.8939e-05 | 5.6585e-06 | 123.784 | 2.3324e-05 | 571.1127 | 6060.1398 | 0 | 0.10679
[10 empty] | Compound A | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 1.5795e-07
[10 empty] | Compound B | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 1.5795e-07
[10 empty] | Compound C | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 1.5795e-07
[10 empty] | n-Butane (VOC Surrogate) | 866.9903 | 1.5205 | 6.824e-06 | 6.1348e-05 | 0.0078114 | 0.00018404 | 6.0825e-05 | 6.8239e-06 | 38.8102 | 2.8865e-05 | 178.9729 | 1974.1708 | 0 | 0.00012261
[10 empty] | Average volumetric air flow rate, m3/s | 4.5848
[10 empty] | Fraction of area agitated (Vav), ft2 | 3162.852
[10 empty] | F/D | 5.6419
[10 empty] | Effective Diameter (de) | 39.5033
[10 empty] | U* | 0.13347
[10 empty] | NH3 KLa, s-1 | 2.2733e-05
[10 empty] | a, m-1 | 0.14286
[10 empty] | NH3 KL, m/s | 0.00015913
QUALITY CONTROL CHECKS
[10 empty] | Pollutant | Influent load, g/s | Effluent load, g/s | Air emission load, g/s | Absorbed load, g/s | Biodegradation rate, g/s | % Load with effluent | % Load air emitted | % Biodegraded | % Load absorbed | Mass balance Check
[10 empty] | Methanol | 1 | 0.41204 | 0.0008268 | 3.0504e-07 | 0.58713 | 41.2043 | 0.08268 | 58.713 | 3.0504e-05 | 100
[10 empty] | Benzene | 1 | 0.083172 | 0.088469 | 4.2599e-05 | 0.82832 | 8.3172 | 8.8469 | 82.8316 | 0.0042599 | 100
[10 empty] | Carbon disulfide | 1 | 0.076533 | 0.43614 | 2.9058e-05 | 0.4873 | 7.6533 | 43.614 | 48.7299 | 0.0029058 | 100
[10 empty] | Methyl ethyl ketone | 1 | 0.41877 | 0.0058981 | 3.0297e-06 | 0.57533 | 41.8774 | 0.58981 | 57.5325 | 0.00030297 | 100
[10 empty] | Naphthalene | 1 | 0.12133 | 0.011671 | 0.0010554 | 0.86594 | 12.1333 | 1.1671 | 86.5941 | 0.10554 | 100
[10 empty] | Cumene | 1 | 0.041131 | 0.1135 | 0.00059374 | 0.84477 | 4.1131 | 11.3505 | 84.477 | 0.059374 | 100
[10 empty] | Ethylbenzene | 1 | 0.057914 | 0.08663 | 0.00030353 | 0.85515 | 5.7914 | 8.663 | 85.5152 | 0.030353 | 100
[10 empty] | Styrene | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | 1,3-Butadiene | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | Ethylene glycol | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | Methyl isobutyl ketone | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | Toluene | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | Phenol | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | n-Hexane | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | Cresols (total) | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | Xylenes | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | Methyl tert-butyl ether | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | Biphenyl, 1,1- | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | Carbonyl sulfide | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | Dichloroethane, 1,2- | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | Diethanolamine | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | Trimethylpentane, 2,2,4- | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | Compound A | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | Compound B | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | Compound C | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | n-Butane (VOC Surrogate) | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!

## Bio. Mech. Aer. Act. Sldg.
This sheet is used for biological treatment units with mechanical aeration only. Directions: 1) fill-in the input data (yellow boxes); review default variables and constant (yellow boxes) and change if necessary; 2) record air emissions (green boxes); and 3) record effluent concentrations (light blue boxes) for downstream process unit emission calculations.
CRITICAL INPUTS | VALUE | UNITS | DEFAULT VARIABLES / CONSTANTS | VALUE | UNITS | DEFAULT VALUE | AIR EMISSIONS | VALUE | UNITS | EFFLUENT WATER CONCENTRATION | UNITS
Surface area (A) | 1225 | m2 | Viscosity of water (mL) | 0.00893 | g/cm-s | 0.00893 | Methanol | 0.005677 | g/s | 0.42814 | g/m3
Temperature (T) | 25 | deg. C | Density of water (ρL) | 1 | g/cm3 | 1 | Benzene | 0.29197 | g/s | 0.065026 | g/m3
Total pressure (Po) | 1 | atm | Universal gas constant (R ) | 8.21e-05 | atm-m3/gmol-K | 8.21e-05 | Carbon disulfide | 0.48008 | g/s | 0.071391 | g/m3
Wastewater flow rate (Q) | 1 | m3/s | Viscosity of air (ma) | 0.000181 | g/cm-s | 0.000181 | Methyl ethyl ketone | 0.046701 | g/s | 0.41957 | g/m3
Wastewater depth (D) | 7 | m | Density of air (ρa) | 0.0012 | g/cm3 | 0.0012 | Naphthalene | 0.077779 | g/s | 0.1076 | g/m3
Total power to aerators (Ptot) | 300 | hp | Quiescent area (AQ) [default=A-AT] | 725 | m2 | 725 | Cumene | 0.18869 | g/s | 0.036356 | g/m3
Number of aerators (Naer) | 5 | number | Oxygen transfer correction factor (Ot) | 0.83 | dimensionless | 0.83 | Ethylbenzene | 0.22216 | g/s | 0.04858 | g/m3
Biological treatment unit volatile suspended solids (CMLVSS) | 3000 | g/m3 | Oxygen transfer rating to surface area (J) | 3 | lb O2/hp-hr | 3 | Styrene | 0.60355 | g/s | 0.20956 | g/m3
Windspeed (U10) | 4.47 | m/s | Impeller diameter (d) | 61 | cm | 61 | 1,3-Butadiene | 0.56225 | g/s | 0.07463 | g/m3
Wasted sludge volumetric flow rate (Qw) | 0.1 | m3/s | Impeller diameter (d*) | 2 | ft | 2 | Ethylene glycol | 4.0561e-06 | g/s | 0.75079 | g/m3
Turbulent area (AT) | 500 | m2 | Rotational speed of impeller (w) | 126 | rad/s | 126 | Methyl isobutyl ketone | 0.06435 | g/s | 0.25294 | g/m3
Influent 5-day biochemcial oxygen demand concentration (CBOD5,i) | 250 | g/m3 | Diffusivity of ether in water (Dether) | 8.5e-06 | cm2/sec | 8.5e-06 | Toluene | 0.20146 | g/s | 0.043976 | g/m3
Wasted sludge volatile suspended solids (CWAS,VSS) | 15000 | g/m3 | Weight fraction of carbon in biomass (foc) | 0.33 | dimensionless | 0.33 | Phenol | 9.2123e-06 | g/s | 0.010676 | g/m3
|  |  | Biomass volatile suspend solids yield from influent BOD (Y) | 0.67 | g VSS/g BOD | 0.67 | n-Hexane | 0.32067 | g/s | 0.049541 | g/m3
[7 empty] | Cresols (total) | 2.6453e-05 | g/s | 0.0082204 | g/m3
CONSTITUENT INFLUENT CONCENTRATIONS (C0) | [6 empty] | Xylenes | 0.23732 | g/s | 0.054159 | g/m3
Methanol | 1 | g/m3 |  |  |  |  | Methyl tert-butyl ether | 0.15055 | g/s | 0.14199 | g/m3
Benzene | 1 | g/m3 |  |  |  |  | Biphenyl, 1,1- | 0.029478 | g/s | 0.079491 | g/m3
Carbon disulfide | 1 | g/m3 |  |  |  |  | Carbonyl sulfide | 0.52456 | g/s | 0.065418 | g/m3
Methyl ethyl ketone | 1 | g/m3 |  |  |  |  | Dichloroethane, 1,2- | 0.22454 | g/s | 0.10216 | g/m3
Naphthalene | 1 | g/m3 |  |  |  |  | Diethanolamine | 4.6375e-08 | g/s | 0.59541 | g/m3
Cumene | 1 | g/m3 |  |  |  |  | Trimethylpentane, 2,2,4- | 0.034111 | g/s | 0.0056298 | g/m3
Ethylbenzene | 1 | g/m3 |  |  |  |  | Compound A | #DIV/0! | g/s | #DIV/0! | g/m3
Styrene | 1 | g/m3 |  |  |  |  | Compound B | #DIV/0! | g/s | #DIV/0! | g/m3
1,3-Butadiene | 1 | g/m3 |  |  |  |  | Compound C | #DIV/0! | g/s | #DIV/0! | g/m3
Ethylene glycol | 1 | g/m3 |  |  |  |  | n-Butane (VOC Surrogate) | 0.39598 | g/s | 0.052413 | g/m3
Methyl isobutyl ketone | 1 | g/m3
Toluene | 1 | g/m3
Phenol | 1 | g/m3
n-Hexane | 1 | g/m3
Cresols (total) | 1 | g/m3
Xylenes | 1 | g/m3
Methyl tert-butyl ether | 1 | g/m3
Biphenyl, 1,1- | 1 | g/m3
Carbonyl sulfide | 1 | g/m3
Dichloroethane, 1,2- | 1 | g/m3
Diethanolamine | 1 | g/m3
Trimethylpentane, 2,2,4- | 1 | g/m3
Compound A | 1 | g/m3
Compound B | 1 | g/m3
Compound C | 1 | g/m3 | [7 empty] | Windspeed (U10) | 4.47 | m/s
n-Butane (VOC Surrogate) | 1 | g/m3
[10 empty] | INTERMEDIATE OUTPUTS | ScL | ScG | kl,q | kg,q | kl,t | kg,t | Keq | KT | KQ | KOL | a | b | c | kabs | a1 | b1 | c1
[10 empty] | Methanol | 544.5122 | 1.0056 | 8.349e-06 | 0.010305 | 0.019124 | 0.13068 | 0.00018588 | 2.426e-05 | 1.558e-06 | 1.0824e-05 | 0.91331 | 209.8225 | -90 | 3.0797e-08 | 1.0133 | 209.8186 | -90
[10 empty] | Benzene | 911.2245 | 1.714 | 6.6809e-06 | 0.0072089 | 0.014783 | 0.10009 | 0.22793 | 0.0089705 | 6.6539e-06 | 0.0036654 | 5.4221 | 208.3559 | -13.5714 | 2.1307e-05 | 5.4921 | 207.9498 | -13.5714
[10 empty] | Carbon disulfide | 893 | 1.4503 | 6.7386e-06 | 0.0080626 | 0.014933 | 0.10881 | 1.2347 | 0.01344 | 6.734e-06 | 0.0054895 | 7.6484 | 239.2858 | -17.1219 | 1.5795e-05 | 7.7262 | 238.906 | -17.1219
[10 empty] | Methyl ethyl ketone | 911.2245 | 1.8667 | 6.6809e-06 | 0.0068082 | 0.014783 | 0.095912 | 0.0022837 | 0.00021583 | 4.6729e-06 | 9.0861e-05 | 1.0118 | 23.4092 | -10 | 3.0096e-07 | 1.1113 | 23.405 | -10
[10 empty] | Naphthalene | 1190.6667 | 2.5565 | 5.9698e-06 | 0.0055149 | 0.012933 | 0.081958 | 0.019732 | 0.0014374 | 5.6593e-06 | 0.00059006 | 2.1656 | 394.4559 | -42.47 | 0.00036184 | 1.7575 | 372.8765 | -42.47
[10 empty] | Cumene | 1257.7465 | 1.7539 | 5.8354e-06 | 0.0070987 | 0.012583 | 0.09895 | 0.59645 | 0.010372 | 5.8274e-06 | 0.0042368 | 6.9909 | 296.7132 | -10.7966 | 0.0006005 | 6.2476 | 287.609 | -10.7966
[10 empty] | Ethylbenzene | 1144.8718 | 2.0111 | 6.0682e-06 | 0.0064767 | 0.013189 | 0.092406 | 0.32192 | 0.0091375 | 6.0506e-06 | 0.0037332 | 5.8002 | 66.3733 | -3.2381 | 0.00021803 | 5.594 | 65.3819 | -3.2381
[10 empty] | Styrene | 1116.25 | 2.1244 | 6.1328e-06 | 0.0062432 | 0.013357 | 0.089908 | 0.11235 | 0.0057514 | 6.0796e-06 | 0.0023511 | 3.9864 | 1348.3132 | -282.7273 | 0.00013757 | 3.8933 | 1293.6966 | -282.7273
[10 empty] | 1,3-Butadiene | 826.8519 | 0.60576 | 6.9637e-06 | 0.014472 | 0.015519 | 0.16837 | 3.0068 | 0.015058 | 6.9626e-06 | 0.0061501 | 8.457 | 294.7746 | -22.046 | 1.5435e-05 | 8.5353 | 294.2967 | -22.046
[10 empty] | Ethylene glycol | 633.3333 | 0.9883 | 7.8142e-06 | 0.010425 | 0.017732 | 0.13182 | 7.3536e-08 | 9.6933e-09 | 7.6655e-10 | 4.4101e-09 | 0.90001 | 385.2751 | -289.769 | 1.4405e-09 | 1 | 385.2745 | -289.769
[10 empty] | Methyl isobutyl ketone | 1144.8718 | 2.0111 | 6.0682e-06 | 0.0064767 | 0.013189 | 0.092406 | 0.005639 | 0.00050127 | 5.2036e-06 | 0.00020768 | 1.1581 | 6.1856 | -1.6387 | 2.4463e-06 | 1.2546 | 6.18 | -1.6387
[10 empty] | Toluene | 1038.3721 | 1.7337 | 6.3218e-06 | 0.0071539 | 0.013849 | 0.099524 | 0.27126 | 0.0091533 | 6.3012e-06 | 0.0037398 | 5.6144 | 695.9714 | -30.6167 | 8.8821e-05 | 5.5897 | 692.1527 | -30.6167
[10 empty] | Phenol | 981.3187 | 1.8394 | 6.4743e-06 | 0.0068757 | 0.014246 | 0.096622 | 1.6219e-05 | 1.5669e-06 | 1.0963e-07 | 7.0443e-07 | 0.90802 | 698.921 | -7.4615 | 4.77e-06 | 1.0013 | 698.8711 | -7.4615
[10 empty] | n-Hexane | 1149.2921 | 0.75417 | 6.0584e-06 | 0.012496 | 0.013163 | 0.1509 | 4.984 | 0.012937 | 6.0578e-06 | 0.005284 | 9.7421 | 209.8407 | -10.4197 | 0.0015795 | 7.6241 | 186.7301 | -10.4197
[10 empty] | Cresols (total) | 960.2151 | 2.1734 | 6.5341e-06 | 0.0061486 | 0.014401 | 0.088889 | 6.6182e-05 | 5.8804e-06 | 3.8307e-07 | 2.6269e-06 | 0.90345 | 164.5765 | -1.3529 | 1.5795e-07 | 1.0032 | 164.5762 | -1.3529
[10 empty] | Xylenes | 956.1028 | 2.1125 | 6.546e-06 | 0.0062667 | 0.014432 | 0.090161 | 0.2468 | 0.0087543 | 6.5184e-06 | 0.003577 | 5.6323 | 418.2153 | -22.6667 | 0.00023362 | 5.4042 | 410.7792 | -22.6667
[10 empty] | Methyl tert-butyl ether | 850.4762 | 1.473 | 6.8803e-06 | 0.0079793 | 0.015302 | 0.10797 | 0.022678 | 0.0021109 | 6.6283e-06 | 0.00086551 | 1.9791 | 173.2451 | -24.6393 | 1.2589e-05 | 2.0615 | 172.8096 | -24.6393
[10 empty] | Biphenyl, 1,1- | 1089.0244 | 3.7335 | 6.1965e-06 | 0.004279 | 0.013523 | 0.06782 | 0.011439 | 0.00073369 | 5.5002e-06 | 0.00030272 | 2.6342 | 170.5204 | -13.5714 | 0.0009089 | 1.4579 | 153.199 | -13.5714
[10 empty] | Carbonyl sulfide | 686.9231 | 0.9328 | 7.543e-06 | 0.010837 | 0.017027 | 0.13568 | 2.01 | 0.016026 | 7.5404e-06 | 0.0065457 | 8.92 | 261.1463 | -17.1219 | 9.9865e-07 | 9.0186 | 261.1223 | -17.1219
[10 empty] | Dichloroethane, 1,2- | 902.0202 | 1.4503 | 6.7098e-06 | 0.0080626 | 0.014859 | 0.10881 | 0.057194 | 0.0043863 | 6.6136e-06 | 0.0017942 | 3.1051 | 20.6593 | -2.1429 | 4.77e-06 | 3.1984 | 20.6449 | -2.1429
[10 empty] | Diethanolamine | 911.2245 | 2.1425 | 6.6809e-06 | 0.0062078 | 0.014783 | 0.089527 | 1.581e-09 | 1.4154e-10 | 9.8145e-12 | 6.3581e-11 | 0.90001 | 118.5572 | -70.9091 | 5.8683e-09 | 1 | 118.5566 | -70.9091
[10 empty] | Trimethylpentane, 2,2,4- | 1355.0835 | 2.0578 | 5.6585e-06 | 0.006378 | 0.012123 | 0.091352 | 123.784 | 0.01211 | 5.6585e-06 | 0.0049461 | 167.1378 | 1849.8531 | -10.4197 | 0.10679 | 17.2842 | 287.3847 | -10.4197
[10 empty] | Compound A | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 1.5795e-07 | #DIV/0! | #DIV/0! | 0
[10 empty] | Compound B | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 1.5795e-07 | #DIV/0! | #DIV/0! | 0
[10 empty] | Compound C | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 1.5795e-07 | #DIV/0! | #DIV/0! | 0
[10 empty] | n-Butane (VOC Surrogate) | 866.9903 | 1.5205 | 6.824e-06 | 0.0078114 | 0.015156 | 0.10627 | 38.8102 | 0.0151 | 6.8239e-06 | 0.0061674 | 8.639 | 198.3465 | -10.4197 | 0.00012261 | 8.5668 | 196.5525 | -10.4197
[10 empty] | Power number (P) | 0.00022507
[10 empty] | Reynolds number (Re) | 3108371.2707
[10 empty] | Froude number (Fr) | 987.0065
[10 empty] | Fraction of area agitated (Vav), ft2 | 5379
[10 empty] | F/D | 5.6419
[10 empty] | Effective Diameter (de) | 39.5033
[10 empty] | U* | 0.13347
[10 empty] | WAS VSS, g/m3 | 15000
[10 empty] | Predicted BOD Removal Effic. | 0.57167
QUALITY CONTROL CHECKS
[10 empty] | Pollutant | Influent load, g/s | Effluent load, g/s | Air emission load, g/s | Absorbed load, g/s | Biodegradation rate, g/s | % Load with effluent | % Load air emitted | % Biodegraded | % Load absorbed | Mass balance check
[10 empty] | Methanol | 1 | 0.38532 | 0.005677 | 1.9778e-05 | 0.60898 | 38.5322 | 0.5677 | 60.8981 | 0.0019778 | 100
[10 empty] | Benzene | 1 | 0.058523 | 0.29197 | 0.0020782 | 0.64743 | 5.8523 | 29.1972 | 64.7427 | 0.20782 | 100
[10 empty] | Carbon disulfide | 1 | 0.064252 | 0.48008 | 0.0016914 | 0.45397 | 6.4252 | 48.0083 | 45.3973 | 0.16914 | 100
[10 empty] | Methyl ethyl ketone | 1 | 0.37762 | 0.046701 | 0.00018941 | 0.57549 | 37.7616 | 4.6701 | 57.5494 | 0.018941 | 100
[10 empty] | Naphthalene | 1 | 0.096843 | 0.077779 | 0.058403 | 0.76698 | 9.6843 | 7.7779 | 76.6975 | 5.8403 | 100
[10 empty] | Cumene | 1 | 0.032721 | 0.18869 | 0.032748 | 0.74584 | 3.2721 | 18.8693 | 74.5838 | 3.2748 | 100
[10 empty] | Ethylbenzene | 1 | 0.043722 | 0.22216 | 0.015888 | 0.71823 | 4.3722 | 22.2164 | 71.8227 | 1.5888 | 100
[10 empty] | Styrene | 1 | 0.1886 | 0.60355 | 0.043243 | 0.1646 | 18.8604 | 60.3553 | 16.4601 | 4.3243 | 100
[10 empty] | 1,3-Butadiene | 1 | 0.067167 | 0.56225 | 0.0017279 | 0.36886 | 6.7167 | 56.2249 | 36.8857 | 0.17279 | 100
[10 empty] | Ethylene glycol | 1 | 0.67571 | 4.0561e-06 | 1.6223e-06 | 0.32428 | 67.5713 | 0.00040561 | 32.4281 | 0.00016223 | 100
[10 empty] | Methyl isobutyl ketone | 1 | 0.22765 | 0.06435 | 0.00092816 | 0.70708 | 22.7645 | 6.435 | 70.7077 | 0.092816 | 100
[10 empty] | Toluene | 1 | 0.039578 | 0.20146 | 0.0058589 | 0.7531 | 3.9578 | 20.1462 | 75.3101 | 0.58589 | 100
[10 empty] | Phenol | 1 | 0.0096081 | 9.2123e-06 | 7.6383e-05 | 0.99031 | 0.96081 | 0.00092123 | 99.0306 | 0.0076383 | 100
[10 empty] | n-Hexane | 1 | 0.044587 | 0.32067 | 0.11737 | 0.51736 | 4.4587 | 32.0674 | 51.7365 | 11.7374 | 100
[10 empty] | Cresols (total) | 1 | 0.0073983 | 2.6453e-05 | 1.9476e-06 | 0.99257 | 0.73983 | 0.0026453 | 99.2573 | 0.00019476 | 100
[10 empty] | Xylenes | 1 | 0.048743 | 0.23732 | 0.018979 | 0.69496 | 4.8743 | 23.7317 | 69.496 | 1.8979 | 100
[10 empty] | Methyl tert-butyl ether | 1 | 0.12779 | 0.15055 | 0.0026813 | 0.71898 | 12.7792 | 15.0546 | 71.898 | 0.26813 | 100
[10 empty] | Biphenyl, 1,1- | 1 | 0.071542 | 0.029478 | 0.10837 | 0.79061 | 7.1542 | 2.9478 | 79.0608 | 10.8373 | 100
[10 empty] | Carbonyl sulfide | 1 | 0.058876 | 0.52456 | 9.7995e-05 | 0.41647 | 5.8876 | 52.4557 | 41.6469 | 0.0097995 | 100
[10 empty] | Dichloroethane, 1,2- | 1 | 0.091941 | 0.22454 | 0.00073093 | 0.68279 | 9.1941 | 22.4535 | 68.2792 | 0.073093 | 100
[10 empty] | Diethanolamine | 1 | 0.53587 | 4.6375e-08 | 5.2411e-06 | 0.46413 | 53.5868 | 4.6375e-06 | 46.4126 | 0.00052411 | 100
[10 empty] | Trimethylpentane, 2,2,4- | 1 | 0.0050669 | 0.034111 | 0.90178 | 0.059041 | 0.50669 | 3.4111 | 5.9041 | 90.1781 | 100
[10 empty] | Compound A | 1 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | Compound B | 1 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | Compound C | 1 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | n-Butane (VOC Surrogate) | 1 | 0.047172 | 0.39598 | 0.0096393 | 0.54721 | 4.7172 | 39.5984 | 54.7205 | 0.96393 | 100

## Quiescent Unit
This sheet is used for uncovered quiescent tanks and surface impoundments only. Directions: 1) fill-in the input data (yellow boxes); review default variables and constant (yellow boxes) and change if necessary; 2) record air emissions (green boxes); and 3) record effluent concentrations (light blue boxes) for downstream process unit emission calculations.
CRITICAL INPUTS | VALUE | UNITS | DEFAULT VARIABLES / CONSTANTS | VALUE | UNITS | DEFAULT VALUE | AIR EMISSIONS | VALUE | UNITS | EFFLUENT WATER CONCENTRATION | UNITS
Surface area (A) | 20000 | m2 | Viscosity of water (mL) | 0.00893 | g/cm-s | 0.00893 | Methanol | 0.0069713 | g/s | 0.26078 | g/m3
Temperature (T) | 25 | deg. C | Density of water (ρL) | 1 | g/cm3 | 1 | Benzene | 0.0051087 | g/s | 0.050379 | g/m3
Total pressure (Po) | 1 | atm | Universal gas constant (R ) | 8.21e-05 | atm-m3/gmol-K | 8.21e-05 | Carbon disulfide | 0.0076577 | g/s | 0.074281 | g/m3
Wastewater flow rate (Q) | 0.0876 | m3/s | Viscosity of air (ma) | 0.000181 | g/cm-s | 0.000181 | Methyl ethyl ketone | 0.01705 | g/s | 0.23147 | g/m3
Wastewater depth (D) | 4 | m | Density of air (ρa) | 0.0012 | g/cm3 | 0.0012 | Naphthalene | 0.0055786 | g/s | 0.068503 | g/m3
Biological treatment unit volatile suspended solids (CMLVSS) | 50 | g/m3 | Diffusivity of ether in water (Dether) | 8.5e-06 | cm2/sec | 8.5e-06 | Cumene | 0.0021359 | g/s | 0.026047 | g/m3
Windspeed (U10) | 4.47 | m/s | Weight fraction of carbon in biomass (foc) | 0.33 | dimensionless | 0.33 | Ethylbenzene | 0.0030759 | g/s | 0.035277 | g/m3
Influent 5-day biochemcial oxygen demand concentration (CBOD5,i) | 20 | g/m3 | Biomass volatile suspend solids yield from influent BOD (Y) | 0.67 | g VSS/g BOD | 0.67 | Styrene | 0.025931 | g/s | 0.29386 | g/m3
Note: Set CMLVSS = 0 for a non-biologically active unit | [6 empty] | 1,3-Butadiene | 0.0098644 | g/s | 0.090859 | g/m3
[7 empty] | Ethylene glycol | 7.4396e-06 | g/s | 0.56584 | g/m3
[7 empty] | Methyl isobutyl ketone | 0.010723 | g/s | 0.1398 | g/m3
CONSTITUENT INFLUENT CONCENTRATIONS (C0) | [6 empty] | Toluene | 0.0028646 | g/s | 0.030794 | g/m3
Methanol | 1 | g/m3 |  |  |  |  | Phenol | 1.1314e-05 | g/s | 0.0060321 | g/m3
Benzene | 1 | g/m3 |  |  |  |  | n-Hexane | 0.0042412 | g/s | 0.048651 | g/m3
Carbon disulfide | 1 | g/m3 |  |  |  |  | Cresols (total) | 3.0175e-05 | g/s | 0.0046304 | g/m3
Methyl ethyl ketone | 1 | g/m3 |  |  |  |  | Xylenes | 0.0039414 | g/s | 0.040137 | g/m3
Naphthalene | 1 | g/m3 |  |  |  |  | Methyl tert-butyl ether | 0.0092126 | g/s | 0.08942 | g/m3
Cumene | 1 | g/m3 |  |  |  |  | Biphenyl, 1,1- | 0.0041553 | g/s | 0.05093 | g/m3
Ethylbenzene | 1 | g/m3 |  |  |  |  | Carbonyl sulfide | 0.0089674 | g/s | 0.073007 | g/m3
Styrene | 1 | g/m3 |  |  |  |  | Dichloroethane, 1,2- | 0.0071294 | g/s | 0.070481 | g/m3
1,3-Butadiene | 1 | g/m3 |  |  |  |  | Diethanolamine | 7.0522e-08 | g/s | 0.41893 | g/m3
Ethylene glycol | 1 | g/m3 |  |  |  |  | Trimethylpentane, 2,2,4- | 0.0035725 | g/s | 0.045733 | g/m3
Methyl isobutyl ketone | 1 | g/m3 |  |  |  |  | Compound A | #DIV/0! | g/s | #DIV/0! | g/m3
Toluene | 1 | g/m3 |  |  |  |  | Compound B | #DIV/0! | g/s | #DIV/0! | g/m3
Phenol | 1 | g/m3 |  |  |  |  | Compound C | #DIV/0! | g/s | #DIV/0! | g/m3
n-Hexane | 1 | g/m3 |  |  |  |  | n-Butane (VOC Surrogate) | 0.0050721 | g/s | 0.048212 | g/m3
Cresols (total) | 1 | g/m3
Xylenes | 1 | g/m3
Methyl tert-butyl ether | 1 | g/m3
Biphenyl, 1,1- | 1 | g/m3
Carbonyl sulfide | 1 | g/m3
Dichloroethane, 1,2- | 1 | g/m3
Diethanolamine | 1 | g/m3
Trimethylpentane, 2,2,4- | 1 | g/m3
Compound A | 1 | g/m3
Compound B | 1 | g/m3
Compound C | 1 | g/m3
n-Butane (VOC Surrogate) | 1 | g/m3
[10 empty] | Windspeed (U10) | 4.47 | m/s
[10 empty] | INTERMEDIATE OUTPUTS | ScL | ScG | kl,q | kg,q | Keq | KQ | KOL | kabs | a1 | b1 | c1
[10 empty] | Methanol | 544.5122 | 1.0056 | 7.1727e-06 | 0.0088376 | 0.00018588 | 1.3366e-06 | 1.3366e-06 | 3.0797e-08 | 1.3052 | 344.7753 | -90
[10 empty] | Benzene | 911.2245 | 1.714 | 5.0887e-06 | 0.0061824 | 0.22793 | 5.0704e-06 | 5.0704e-06 | 2.1307e-05 | 2.1579 | 269.2802 | -13.5714
[10 empty] | Carbon disulfide | 893 | 1.4503 | 5.1577e-06 | 0.0069146 | 1.2347 | 5.1546e-06 | 5.1546e-06 | 1.5795e-05 | 2.1771 | 230.3392 | -17.1219
[10 empty] | Methyl ethyl ketone | 911.2245 | 1.8667 | 5.0887e-06 | 0.0058388 | 0.0022837 | 3.6831e-06 | 3.6831e-06 | 3.0096e-07 | 1.8409 | 42.7767 | -10
[10 empty] | Naphthalene | 1190.6667 | 2.5565 | 4.2576e-06 | 0.0047296 | 0.019732 | 4.0718e-06 | 4.0718e-06 | 0.00036184 | 1.9345 | 619.8435 | -42.47
[10 empty] | Cumene | 1257.7465 | 1.7539 | 4.1048e-06 | 0.0060879 | 0.59645 | 4.1002e-06 | 4.1002e-06 | 0.0006005 | 1.9442 | 414.4602 | -10.7966
[10 empty] | Ethylbenzene | 1144.8718 | 2.0111 | 4.3704e-06 | 0.0055545 | 0.32192 | 4.3597e-06 | 4.3597e-06 | 0.00021803 | 1.9983 | 91.7213 | -3.2381
[10 empty] | Styrene | 1116.25 | 2.1244 | 4.4447e-06 | 0.0053542 | 0.11235 | 4.4121e-06 | 4.4121e-06 | 0.00013757 | 2.0092 | 961.5204 | -282.7273
[10 empty] | 1,3-Butadiene | 826.8519 | 0.60576 | 5.4292e-06 | 0.012411 | 3.0068 | 5.4284e-06 | 5.4284e-06 | 1.5435e-05 | 2.2396 | 242.4375 | -22.046
[10 empty] | Ethylene glycol | 633.3333 | 0.9883 | 6.4853e-06 | 0.0089407 | 7.3536e-08 | 6.574e-10 | 6.574e-10 | 1.4405e-09 | 1.0002 | 511.5421 | -289.769
[10 empty] | Methyl isobutyl ketone | 1144.8718 | 2.0111 | 4.3704e-06 | 0.0055545 | 0.005639 | 3.8352e-06 | 3.8352e-06 | 2.4463e-06 | 1.8757 | 11.4597 | -1.6387
[10 empty] | Toluene | 1038.3721 | 1.7337 | 4.6643e-06 | 0.0061353 | 0.27126 | 4.6513e-06 | 4.6513e-06 | 8.8821e-05 | 2.0631 | 994.1801 | -30.6167
[10 empty] | Phenol | 981.3187 | 1.8394 | 4.8434e-06 | 0.0058967 | 1.6219e-05 | 9.3784e-08 | 9.3784e-08 | 4.77e-06 | 1.0215 | 1236.9617 | -7.4615
[10 empty] | n-Hexane | 1149.2921 | 0.75417 | 4.3591e-06 | 0.010716 | 4.984 | 4.3588e-06 | 4.3588e-06 | 0.0015795 | 2.0163 | 214.0733 | -10.4197
[10 empty] | Cresols (total) | 960.2151 | 2.1734 | 4.9141e-06 | 0.0052731 | 6.6182e-05 | 3.2584e-07 | 3.2584e-07 | 1.5795e-07 | 1.0744 | 292.1837 | -1.3529
[10 empty] | Xylenes | 956.1028 | 2.1125 | 4.9282e-06 | 0.0053744 | 0.2468 | 4.9099e-06 | 4.9099e-06 | 0.00023362 | 2.1241 | 564.6504 | -22.6667
[10 empty] | Methyl tert-butyl ether | 850.4762 | 1.473 | 5.3282e-06 | 0.0068431 | 0.022678 | 5.1513e-06 | 5.1513e-06 | 1.2589e-05 | 2.1763 | 275.3513 | -24.6393
[10 empty] | Biphenyl, 1,1- | 1089.0244 | 3.7335 | 4.5185e-06 | 0.0036697 | 0.011439 | 4.0794e-06 | 4.0794e-06 | 0.0009089 | 1.9435 | 266.3712 | -13.5714
[10 empty] | Carbonyl sulfide | 686.9231 | 0.9328 | 6.1435e-06 | 0.0092937 | 2.01 | 6.1415e-06 | 6.1415e-06 | 9.9865e-07 | 2.4022 | 234.3491 | -17.1219
[10 empty] | Dichloroethane, 1,2- | 902.0202 | 1.4503 | 5.1232e-06 | 0.0069146 | 0.057194 | 5.0577e-06 | 5.0577e-06 | 4.77e-06 | 2.1548 | 30.2522 | -2.1429
[10 empty] | Diethanolamine | 911.2245 | 2.1425 | 5.0887e-06 | 0.0053239 | 1.581e-09 | 8.4171e-12 | 8.4171e-12 | 5.8683e-09 | 1 | 168.8453 | -70.9091
[10 empty] | Trimethylpentane, 2,2,4- | 1355.0835 | 2.0578 | 3.9058e-06 | 0.0054698 | 123.784 | 3.9058e-06 | 3.9058e-06 | 0.10679 | 3.3227 | 227.685 | -10.4197
[10 empty] | Compound A | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | 1.5795e-07 | #DIV/0! | #DIV/0! | 0
[10 empty] | Compound B | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | 1.5795e-07 | #DIV/0! | #DIV/0! | 0
[10 empty] | Compound C | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | 1.5795e-07 | #DIV/0! | #DIV/0! | 0
[10 empty] | n-Butane (VOC Surrogate) | 866.9903 | 1.5205 | 5.2603e-06 | 0.0066991 | 38.8102 | 5.2602e-06 | 5.2602e-06 | 0.00012261 | 2.2026 | 216.0143 | -10.4197
[10 empty] | F/D | 39.8942
[10 empty] | Effective Diameter (de) | 159.6174
[10 empty] | U* | 0.13347
[10 empty] | Predicted BOD Removal Effic. | 1
QUALITY CONTROL CHECKS
[10 empty] | Pollutant | Influent load, g/s | Effluent load, g/s | Air emission load, g/s | Absorbed load, g/s | Biodegradation rate, g/s | % Load with effluent | % Load air emitted | % Biodegraded | % Load absorbed | Mass balance check
[10 empty] | Methanol | 0.0876 | 0.022845 | 0.0069713 | 1.0762e-07 | 0.057784 | 26.0782 | 7.9581 | 65.9636 | 0.00012285 | 100.0001
[10 empty] | Benzene | 0.0876 | 0.0044132 | 0.0051087 | 1.4383e-05 | 0.078077 | 5.0379 | 5.8319 | 89.1288 | 0.01642 | 100.015
[10 empty] | Carbon disulfide | 0.0876 | 0.006507 | 0.0076577 | 1.5722e-05 | 0.073434 | 7.4281 | 8.7417 | 83.8286 | 0.017947 | 100.0164
[10 empty] | Methyl ethyl ketone | 0.0876 | 0.020276 | 0.01705 | 9.3348e-07 | 0.050273 | 23.1466 | 19.4636 | 57.3896 | 0.0010656 | 100.001
[10 empty] | Naphthalene | 0.0876 | 0.0060008 | 0.0055786 | 0.00033214 | 0.075991 | 6.8503 | 6.3682 | 86.7483 | 0.37916 | 100.3459
[10 empty] | Cumene | 0.0876 | 0.0022817 | 0.0021359 | 0.00020959 | 0.083164 | 2.6047 | 2.4383 | 94.9361 | 0.23926 | 100.2183
[10 empty] | Ethylbenzene | 0.0876 | 0.0030902 | 0.0030759 | 0.00010306 | 0.081425 | 3.5277 | 3.5113 | 92.9507 | 0.11765 | 100.1073
[10 empty] | Styrene | 0.0876 | 0.025742 | 0.025931 | 0.0005417 | 0.035879 | 29.3861 | 29.6018 | 40.9579 | 0.61838 | 100.5642
[10 empty] | 1,3-Butadiene | 0.0876 | 0.0079592 | 0.0098644 | 1.8793e-05 | 0.069775 | 9.0859 | 11.2607 | 79.6516 | 0.021453 | 100.0196
[10 empty] | Ethylene glycol | 0.0876 | 0.049567 | 7.4396e-06 | 1.0922e-08 | 0.038025 | 56.5836 | 0.0084927 | 43.4079 | 1.2468e-05 | 100
[10 empty] | Methyl isobutyl ketone | 0.0876 | 0.012246 | 0.010723 | 4.5826e-06 | 0.06463 | 13.9796 | 12.2409 | 73.779 | 0.0052313 | 100.0048
[10 empty] | Toluene | 0.0876 | 0.0026975 | 0.0028646 | 3.6651e-05 | 0.082035 | 3.0794 | 3.2701 | 93.6468 | 0.041839 | 100.0382
[10 empty] | Phenol | 0.0876 | 0.00052841 | 1.1314e-05 | 3.8556e-07 | 0.08706 | 0.60321 | 0.012916 | 99.3838 | 0.00044013 | 100.0004
[10 empty] | n-Hexane | 0.0876 | 0.0042618 | 0.0042412 | 0.0010297 | 0.079007 | 4.8651 | 4.8415 | 90.1904 | 1.1755 | 101.0725
[10 empty] | Cresols (total) | 0.0876 | 0.00040562 | 3.0175e-05 | 9.8002e-09 | 0.087164 | 0.46304 | 0.034447 | 99.5025 | 1.1187e-05 | 100
[10 empty] | Xylenes | 0.0876 | 0.003516 | 0.0039414 | 0.00012565 | 0.080132 | 4.0137 | 4.4993 | 91.4745 | 0.14344 | 100.1309
[10 empty] | Methyl tert-butyl ether | 0.0876 | 0.0078332 | 0.0092126 | 1.5084e-05 | 0.070553 | 8.942 | 10.5167 | 80.5398 | 0.017219 | 100.0157
[10 empty] | Biphenyl, 1,1- | 0.0876 | 0.0044615 | 0.0041553 | 0.00062029 | 0.078929 | 5.093 | 4.7435 | 90.1014 | 0.7081 | 100.6461
[10 empty] | Carbonyl sulfide | 0.0876 | 0.0063954 | 0.0089674 | 9.7697e-07 | 0.072237 | 7.3007 | 10.2368 | 82.4624 | 0.0011153 | 100.001
[10 empty] | Dichloroethane, 1,2- | 0.0876 | 0.0061741 | 0.0071294 | 4.5049e-06 | 0.074296 | 7.0481 | 8.1386 | 84.8129 | 0.0051426 | 100.0047
[10 empty] | Diethanolamine | 0.0876 | 0.036698 | 7.0522e-08 | 3.2942e-08 | 0.050902 | 41.8925 | 8.0505e-05 | 58.1074 | 3.7606e-05 | 100
[10 empty] | Trimethylpentane, 2,2,4- | 0.0876 | 0.0040062 | 0.0035725 | 0.065441 | 0.074289 | 4.5733 | 4.0782 | 84.8045 | 74.7041 | 168.1601
[10 empty] | Compound A | 0.0876 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | Compound B | 0.0876 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | Compound C | 0.0876 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | n-Butane (VOC Surrogate) | 0.0876 | 0.0042234 | 0.0050721 | 7.9209e-05 | 0.078298 | 4.8212 | 5.7901 | 89.3807 | 0.090422 | 100.0825

## Chemical Properties
DEFAULT PROPERTIES | [9 empty] | Calculated
CAS No. | Compound Name | Mol.Wt. | Vap. Press. (mmHg) | H law const. (atm-m3/mol) | Di,w (cm2/sec) | Di,a (cm2/sec) | log(Kow) | Kb,max (gVO/g-s) | Ks, (g/m3) | Koc
67561 | Methanol | 32.04 | 126 | 4.55e-06 | 1.64e-05 | 0.15 | -0.71 | 5e-06 | 90 | 0.093325
71432 | Benzene | 78.11 | 95 | 0.0055793 | 9.8e-06 | 0.088 | 2.13 | 5.2778e-06 | 13.5714 | 64.5654
75150 | Carbon disulfide | 76.14 | 359 | 0.030224 | 1e-05 | 0.104 | 2 | 4.25e-06 | 17.1219 | 47.863
78933 | Methyl ethyl ketone | 72.11 | 95.3 | 5.59e-05 | 9.8e-06 | 0.0808 | 0.28 | 5.5556e-07 | 10 | 0.91201
91203 | Naphthalene | 128.17 | 0.085 | 0.000483 | 7.5e-06 | 0.059 | 3.36 | 1.1797e-05 | 42.47 | 1096.4782
98828 | Cumene | 120.19 | 4.5 | 0.0146 | 7.1e-06 | 0.086 | 3.58 | 8.6389e-06 | 10.7966 | 1819.7009
100414 | Ethylbenzene | 106.17 | 9.6 | 0.00788 | 7.8e-06 | 0.075 | 3.14 | 1.8889e-06 | 3.2381 | 660.6934
100425 | Styrene | 104.15 | 6.12 | 0.00275 | 8e-06 | 0.071 | 2.94 | 8.6389e-06 | 282.7273 | 416.8694
106990 | 1,3-Butadiene | 54.09 | 2110 | 0.0736 | 1.08e-05 | 0.249 | 1.99 | 4.25e-06 | 22.046 | 46.7735
107211 | Ethylene glycol | 60.0986 | 0.126 | 1.8e-09 | 1.41e-05 | 0.15262 | -2.04 | 4.8778e-06 | 289.769 | 0.0043652
108101 | Methyl isobutyl ketone | 100.16 | 19.9 | 0.00013803 | 7.8e-06 | 0.075 | 1.19 | 2.0556e-07 | 1.6387 | 7.4131
108883 | Toluene | 92.14 | 28.4 | 0.00664 | 8.6e-06 | 0.087 | 2.75 | 2.0411e-05 | 30.6167 | 269.1535
108952 | Phenol | 94.11 | 0.276 | 3.97e-07 | 9.1e-06 | 0.082 | 1.48 | 2.6944e-05 | 7.4615 | 14.4544
110543 | n-Hexane | 86.18 | 151 | 0.122 | 7.77e-06 | 0.2 | 4 | 4.25e-06 | 10.4197 | 4786.3009
1319773 | Cresols (total) | 108.1 | 0.3 | 1.62e-06 | 9.3e-06 | 0.0694 | 0 | 6.3889e-06 | 1.3529 | 0.47863
1330207 | Xylenes | 106.17 | 8.0418 | 0.0060412 | 9.34e-06 | 0.0714 | 3.17 | 1.1333e-05 | 22.6667 | 707.9458
1634044 | Methyl tert-butyl ether | 88 | 185.949 | 0.00055513 | 1.05e-05 | 0.1024 | 1.9015 | 4.8778e-06 | 24.6393 | 38.1478
92524 | Biphenyl, 1,1- | 154.21 | 0.00964 | 0.00028 | 8.2e-06 | 0.0404 | 3.76 | 5.2778e-06 | 13.5714 | 2754.2287
463581 | Carbonyl sulfide | 60.07 | 9412 | 0.0492 | 1.3e-05 | 0.1617 | 0.8009 | 4.2534e-06 | 17.1219 | 3.0262
107062 | Dichloroethane, 1,2- | 98.96 | 79.5 | 0.0014 | 9.9e-06 | 0.104 | 1.48 | 5.833e-07 | 2.1429 | 14.4544
111422 | Diethanolamine | 105.14 | 0.000278 | 3.87e-11 | 9.8e-06 | 0.0704 | -1.43 | 2.1667e-06 | 70.9091 | 0.017783
540841 | Trimethylpentane, 2,2,4- | 114.23 | 49.172 | 3.03 | 6.59e-06 | 0.0733 | 5.83 | 4.25e-06 | 10.4197 | 323593.6569
| Compound A | [8 empty] | 0.47863
| Compound B | [8 empty] | 0.47863
| Compound C | [8 empty] | 0.47863
106978 | n-Butane (VOC Surrogate) | 58.12 | 1820 | 0.95 | 1.03e-05 | 0.0992 | 2.89 | 4.25e-06 | 10.4197 | 371.5352
Color Code:
Data not in HWIR database; used value from CHEMDAT8 constituent input database
Biodegradation reactions are the same as other aromatic hydrocarbons: oxygenase addition of molecular oxygen to one of the aromatic rings (Boyle, 1992). Therefore, the known values for Benzene were substituted.
Biodegradation reactions are the same as other aliphatic compounds (McCarty and Rittman, 2001). Therefore, the known biodegradation constants for n-Hexane were substituted.
Biodegradation reactions are the same as other alcohols (Rittman and McCarty, 2001). Therefore, the known diodegradation constants for Butanol were substituted.
Substituted Carbon disulfide biodegradation constants.
SITE-SPECIFIC PROPERTIES
CAS No. | Compound Name | Mol.Wt. | Vap. Press. (mmHg) | H law const. (atm-m3/mol) | Di,w (cm2/sec) | Di,a (cm2/sec) | log(Kow) | Kb,max (gVO/g-s) | Ks, (g/m3)
67561 | Methanol
71432 | Benzene
75150 | Carbon disulfide
78933 | Methyl ethyl ketone
91203 | Naphthalene
98828 | Cumene
100414 | Ethylbenzene
100425 | Styrene
106990 | 1,3-Butadiene
107211 | Ethylene glycol
108101 | Methyl isobutyl ketone
108883 | Toluene
108952 | Phenol
110543 | n-Hexane
1319773 | Cresols (total)
1330207 | Xylenes
1634044 | Methyl tert-butyl ether
92524 | Biphenyl, 1,1-
463581 | Carbonyl sulfide
107062 | Dichloroethane, 1,2-
111422 | Diethanolamine
540841 | Trimethylpentane, 2,2,4-
Compound A
Compound B
Compound C
106978 | n-Butane (VOC Surrogate)
References:
Boyle, A.W., et al. (1992). "Bacterial PCB Biodegradation." Biodegradation 3(2/3), pp. 285-298.
Rittman, B.E. and McCarty, P.L. (2001). "Environmental Biotechnology: Principles and Applications". McGraw-Hill, New York, NY.